PV I-V CHARACTERISTIC

TESTER

[Graduation Project]

[This project is a partial fulfillment of B.Sc. Degree of Electrical Engineering

Department of An-Najah National University]

Done By:
                      Tamer Jaber

Supervised by:

Prof.Marwan M.Mahmoud

إليهما...

العَيْـشُ مَاضٍ فَأَكْـرِمْ وَالِدَيْـكَ بِـهِ
والأُمُّ أَوْلَـى بِـإِكْـرَامٍ وَإِحْـسَـانِ
وَحَسْبُهَا الحَمْـلُ وَالإِرْضَـاعُ تُدْمِنُـهُ
أَمْـرَانِ بِالفَضْـلِ نَـالاَ كُلَّ إِنْسَـانِ
إليهما...

أَطِــعِ الإِلَــهَ كَـمَـا أَمَــرْ
وَامْــلأْ فُــؤَادَكَ بِـالحَــذَرْ
وَأَطِــعِ أَبَـــاكَ فَــإِنَّــهُ
رَبَّـاكَ مِـنْ عَـهْـدِ الصِّـغَـرْ

إليهما...
إلى طقوس جبهته السمراء وإلى احمرار عينيها الوضائتين
إلى سهرهم وآهاتهم ودموعهم 
إلى قلوبهم التي ما زلت أحيا من أجله
إلى أجمل حروف نطقتها
إلى أبي وأمي...

إليك أستاذي...
       إِنْ كُنا ناراً يُستضاءُ بِعلمنا................يَكفيكَ فَخراً أَنكَ المَروانُ

إليكما صديقاي يزن و فراس...
أشكركم من كل قلبي على كل ما فعلتموه لأجلي..

إلى كل من كان بجانبي...

تامر جبر

Chapter One

Introduction

M

easuring the I–V characteristics is of high importance since it can be considered as a quality and performance certificate for each PV generator. The most precise and inexpensive measuring method is represented in capacitor charging by the PV generator. Using the equivalent circuit of the PV generator with a capacitor as load and applying transient analysis on the circuit, we obtain the capacitor charging voltage and current as a function of time, as well as their differentials as a function of short circuit current and capacitor size.

The I- V characteristics (or I- V curve) of a PV cell, module or array (PV generator) is the important key for identifying its quality and performance as a function of varying environmental parameters such as solar radiation and ambient temperature. The curve indicates the characteristic parameters of the PV generator represented in short circuit current, open circuit voltage and the point of maximum power at which the generator would work at its peak efficiency. These parameters are indispensable for designing any small or large PV power system. Moreover, the curve render determining the equivalent circuit components of the PV generator represented in the series resistance and shunt resistance, which are disclosure parameters for classifying the quality of the generator substrate material.

Therefore, it is of prime importance to measure the I- V characteristics with high accuracy under natural environmental conditions. The easiest method is to use variable resistor as a load to the PV generator and measure the stepwise voltage and current. The I- V curve obtained by this method is deficient in accuracy, uniformity and smoothness, due to manual change of the load resistor and slowness of the measuring process.

The second measuring method is to load the PV generator by a capacitor and to charge it fully from short circuit to open circuit, and to record the respective voltage and current by X- Y recorder or a computerized data acquisition system (CDAS).

The I-V curve obtained by this method is much more accurate and uniform since it is measured in a very short time. In addition, it surpasses the first method by enabling the measurement of the I-V curve of PV generators of higher power with reasonable capacitor values.

The I- V characteristics (or I- V curve) of a PV cell, module or array (PV generator) is the important key for identifying its quality and performance as a function of varying environmental parameters such as solar radiation and ambient temperature. The curve indicates the characteristic parameters of the PV generator represented in short circuit current, open circuit voltage and the point of maximum power at which the generator would work at its peak efficiency. These parameters are indispensable for designing any small or large PV power system. Moreover, the curve render determining the equivalent circuit components of the PV generator represented in the series resistance and shunt resistance, which are disclosure parameters for classifying the quality of the generator substrate material.

System since the solar cell is still expensive. This thesis proposes the development of IV Curve tester for photovoltaic module, which is capable to measure the Maximum Power of 80 watts. This test set is also able to measure other electric important features of the solar cell; Open Circuit Voltage, Short Circuit Current, Maximum Voltage, Maximum Current and Fill Factor which show the measurement on the computer monitor. The IV Curve from the experiment by measuring and collecting current and voltage data of the solar cell should be good enough to be analyzed to find the electric features of the solar cell.

Chapter Two

Photovoltaic Cells

Photovoltaic Cells.

At the present time, most commercial photovoltaic cells are manufactured from silicon, the same material from which sand is made. In this case, however, the silicon is extremely pure. Other, more exotic materials such as gallium arsenide are just beginning to make their way into the field.

The four general types of silicon photovoltaic cells are:

- Single-crystal silicon.

- Polycrystalline silicon (also known as multicrystal silicon).

- Ribbon silicon.

- Amorphous silicon (abbreviated as "aSi," also known as thin film silicon).

Single-crystal silicon

Most photovoltaic cells are single-crystal types. To make them, silicon is purified, melted, and crystallized into ingots. The ingots are sliced into thin wafers to make individual cells. The cells have a uniform color, usually blue or black

Typically, most of the cell has a slight positive electrical charge. A thin layer at the top has a slight negative charge.

The cell is attached to a base called a "backplane." This is usually a layer of metal used to physically reinforce the cell and to provide an electrical contact at the bottom.

Since the top of the cell must be open to sunlight, a thin grid of metal is applied to the top instead of a continuous layer. The grid must be thin enough to admit adequate amounts of sunlight, but wide enough to carry adequate amounts of electrical energy

Light, including sunlight, is sometimes described as particles called "photons." As sunlight strikes a photovoltaic cell, photons move into the cell.

When a photon strikes an electron, it dislodges it, leaving an empty "hole". The loose electron moves toward the top layer of the cell. As photons continue to enter the cell, electrons continue to be dislodged and move upwards

If an electrical path exists outside the cell between the top grid and the backplane of the cell, a flow of electrons begins. Loose electrons move out the top of the cell and into the external electrical circuit. Electrons from further back in the circuit move up to fill the empty electron holes.

Most cells produce a voltage of about one-half volt, regardless of the surface area of the cell. However, the larger the cell, the more current it will produce.

Current and voltage are affected by the resistance of the circuit the cell is in. The amount of available light affects current production. The temperature of the cell affects its voltage. Knowing the electrical performance characteristics of a photovoltaic power supply is important, and is covered in the next section.

Polycrystalline silicon

Polycrystalline cells are manufactured and operate in a similar manner. The difference is that a lower cost silicon is used. This usually results in slightly lower efficiency, but polycrystalline cell manufacturers assert that the cost benefits outweigh the efficiency losses.

The surface of polycrystalline cells has a random pattern of crystal borders instead of the solid color of single crystal cells (Figure 2-1 3).

Ribbon silicon

Ribbon-type photovoltaic cells are made by growing a ribbon from the molten silicon instead of an ingot. These cells operate the same as single and polycrystal cells.

The anti-reflective coating used on most ribbon silicon cells gives them a prismatic rainbow appearance.

Amorphous or thin film silicon

The previous three types of silicon used for photovoltaic cells have a distinct crystal structure. Amorphous silicon has no such structure. Amorphous silicon is sometimes abbreviated "aSi" and is also called thin film silicon.

Amorphous silicon units are made by depositing very thin layers of vaporized silicon in a vacuum onto a support of glass, plastic, or metal.

Amorphous silicon cells are produced in a variety of colors (Figure 2-1 4).

Since they can be made in sizes up to several square yards, they are made up in long rectangular "strip cells." These are connected in series to make up "module”.

Because the layers of silicon allow some light to pass through, multiple layers can be deposited. The added layers increase the amount of electricity the photovoltaic cell can produce. Each layer can be "tuned" to accept a particular band of light wavelength.

The performance of amorphous silicon cells can drop as much as 15% upon initial exposure to sunlight. This drop takes around six weeks. Manufacturers generally publish post-exposure performance data, so if the module has not been exposed to sunlight, its performance will exceed specifications at first.

The efficiency of amorphous silicon photovoltaic modules is less than half that of the other three technologies. This technology has the potential of being much less expensive to manufacture than crystalline silicon technology. For this reason, research is currently under way to improve

amorphous silicon performance and manufacturing processes.

Photovoltaic Modules

For almost all applications, the one-half volt produced by a single cell is inadequate. Therefore, cells are connected together in series to increase the voltage. Several of these series strings of cells may be connected together in parallel to increase the current as well.

These interconnected cells and their electrical connections are then sandwiched between a top layer of glass or clear plastic and a lower level of plastic or plastic and metal. An outer frame is attached to increase mechanical strength, and to provide a way to mount the unit. This package is called a "module" or "panel" (Figure 2-15). Typically, a module is the basic building block of photovoltaic systems. Table 2-1 is a summary of currently available modules.

Summary of Current Photovoltaic Technology

Groups of modules can be interconnected in series and/or parallel to form an "array." By adding "balance of system" (BOS) components such as storage batteries, charge controllers, and power conditioning devices, we have a complete photovoltaic system.

Describing Photovoltaic Module Performance.

To insure compatibility with storage batteries or loads, it is necessary to know the electrical characteristics of photovoltaic modules.

As a reminder, "I" is the abbreviation for current, expressed in amps. "V" is used for voltage in volts, and "R" is used for resistance in ohms.

A photovoltaic module will produce its maximum current when there is essentially no resistance in the circuit. This would be a short circuit between its positive and negative terminals.

This maximum current is called the short circuit current, abbreviated I(sc). When the module is shorted, the voltage in the circuit is zero.

Conversely, the maximum voltage is produced when there is a break in the circuit. This is called the open circuit voltage, abbreviated V(oc). Under this condition the resistance is infinitely high and there is no current, since the circuit is incomplete.

These two extremes in load resistance, and the whole range of conditions in between them, are depicted on a graph called a I-V (current-voltage) curve. Current, expressed in amps, is on the vertical Y-axis. Voltage, in volts, is on the horizontal X-axis.

As you can see in Figure 2-16, the short circuit current occurs on a point on the curve where the voltage is zero. The open circuit voltage occurs where the current is zero.

The power available from a photovoltaic module at any point along the curve is expressed in watts. Watts are calculated by multiplying the voltage times the current (watts = volts x amps, or W = VA).

At the short circuit current point, the power output is zero, since the voltage is zero.

At the open circuit voltage point, the power output is also zero, but this time it is because the current is zero.

There is a point on the "knee" of the curve where the maximum power output is located. This point on our example curve is where the voltage is 17 volts, and the current is 2.5 amps. Therefore the maximum power in watts is 17 volts times 2.5 amps, equaling 42.5 watts.

The power, expressed in watts, at the maximum power point is described as peak, maximum, or ideal, among other terms. Maximum power is generally abbreviated as "I (mp)." Various manufacturers call it maximum output power, output, peak power, rated power, or other terms.

The current-voltage (I-V) curve is based on the module being under standard conditions of sunlight and module temperature. It assumes there is no shading on the module.

Standard sunlight conditions on a clear day are assumed to be 1000 watts of solar energy per square meter (1000 W/m2or lkW/m2). This is sometimes called "one sun," or a "peak sun." Less than one sun will reduce the current output of the module by a proportional amount. For example, if only one-half sun (500 W/m2) is available, the amount of output current is roughly cut in half

For maximum output, the face of the photovoltaic modules should be pointed as straight toward the sun as possible. Section 2.3.5 contains information on determining the correct direction and module tilt angle for various locations and applications.

Because photovoltaic cells are electrical semiconductors, partial shading of the module will cause the shaded cells to heat up. They are now acting as inefficient conductors instead of electrical generators. Partial shading may ruin shaded cells.

Partial module shading has a serious effect on module power output. For a typical module, completely shading only one cell can reduce the module output by as much as 80%. One or more damaged cells in a module can have the same effect as shading.

This is why modules should be completely unshaded during operation. A shadow across a module can almost stop electricity production. Thin film modules are not as affected by this problem, but they should still be unshaded.

Module temperature affects the output voltage inversely. Higher module temperatures will reduce the voltage by 0.04 to 0.1 volts for every one Celsius degree rise in temperature (0.04V/0C to0.1V/0C). In Fahrenheit degrees, the voltage loss is from 0.022 to 0.056 volts per degree of temperature rise (Figure 2-19).

This is why modules should not be installed flush against a surface. Air should be allowed to circulate behind the back of each module so it's temperature does not rise and reducing its output. An air space of 4-6 inches is usually required to provide proper ventilation.

The last significant factor which determines the power output of a module is the resistance of the system to which it is connected. If the module is charging a battery, it must supply a higher voltage than that of the battery.

If the battery is deeply discharged, the battery voltage is fairly low. The photovoltaic module can charge the battery with a low voltage, shown as point #1 in Figure 2-20. As the battery reaches a full charge, the module is forced to deliver a higher voltage, shown as point #2. The battery voltage drives module voltage.

Eventually, the required voltage is higher than the voltage at the module's maximum power point. At this operating point, the current production is lower than the current at the maximum power point. The module's power output is also lower.

To a lesser degree, when the operating voltage is lower than that of the maximum power point (point #1), the output power is lower than the maximum. Since the ability of the module to produce electricity is not being completely used whenever it is operating at a point fairly far from the maximum power point, photovoltaic modules should be carefully matched to the system load and storage.

Using a module with a maximum voltage which is too high should be avoided nearly as much as using one with a maximum voltage which is too low.

The output voltage of a module depends on the number of cells connected in series. Typical modules use either 30, 32, 33, 36, or 44 cells wired in series.

The modules with 30-32 cells are considered self regulating modules. 36 cell modules are the most common in the photovoltaic industry. Their slightly higher voltage rating, 16.7 volts, allows the modules to overcome the reduction in output voltage when the modules are operating at high temperatures.

Modules with 33 - 36 cells also have enough surplus voltage to effectively charge high antimony content deep cycle batteries. However, since these modules can overcharge batteries, they usually require a charge controller.

Finally, 44 cell modules are available with a rated output voltage of 20.3 volts. These modules are typically used only when a substantially higher voltage is required.

As an example, if the module is sometimes forced to operate at high temperatures, it can still supply enough voltage to charge 1 2 volt batteries.

Another application for 44 cell modules is a system with an extremely long wire run between the modules and the batteries or load. If the wire is not large enough, it will cause a significant voltage drop. Higher module voltage can overcome this problem.

It should be noted that this approach is similar to putting a larger engine in a car with locked brakes to make it move faster. It is almost always more cost effective to use an adequate wire size, rather than to overcome voltage drop problems with more costly 44 cell modules.

Section 2.5.5 discusses maximum power point trackers. These devices are used to bring the module to a point as close as possible to the maximum power point. They are used mostly in direct DC systems, particularly with DC motors for pumping.

Photovoltaic Arrays.

In many applications the power available from one module is inadequate for the load. Individual modules can be connected in series, parallel, or both to increase either output voltage or current. This also increases the output power.

When modules are connected in parallel, the current increases. For example, three modules which produce 15 volts and 3 amps each, connected in parallel, will produce 15 volts and 9 amps

If the system includes a battery storage system, a reverse flow of current from the batteries through the photovoltaic array can occur at night. This flow will drain power from the batteries.

A diode is used to stop this reverse current flow. Diodes are electrical devices which only allow current to flow in one direction. A blocking diode is shown

Diodes with the least amount of voltage drop are called schottky diodes, typically dropping .3 volts instead of .7 volts as in silicon diodes.

Because diodes create a voltage drop, some systems use a controller which opens the circuit instead of using a blocking diode.

If the same three modules are connected in series, the output voltage will be 45 volts, and the current will be 3 amps.

If one module in a series string fails, it provides so much resistance that other modules in the string may not be able to operate either. A bypass path around the disabled module will eliminate this problem (Figure 2-23). The bypass diode allows the current from the other modules to flow through in the "right" direction.

Many modules are supplied with a bypass diode right at their electrical terminals. Larger modules may consist of three groups of cells, each with its own bypass diode

Built in bypass diodes are usually adequate unless the series string produces 48 volts or higher, or serious shading occurs regularly.

Combinations of series and parallel connections are also used in arrays (Figure 2-24). If parallel groups of modules are connected in a series string, large bypass diodes are usually required.

Isolation diodes are used to prevent the power from the rest of an array from flowing through a damaged series string of modules. They operate like a blocking diode. They are normally required when the array produces 48 volts or more. If isolation diodes are used on every series string, a blocking diode is normally not required

Chapter Three

Transient analysis of a PV power generator charging a capacitor for measurement of the I–V characteristics

The power electronic circuit

Chapter Four

The project

The Block diagram of  Project:

Here is the block diagram of the project the operation start from solar cell then a power electronic circuit (mentioned in the next chapter) transfer a values of current and voltage to the PIC which take readings every 5 ms ,in PIC the value entered convert to digital value through the ADC which built in the PIC and stored one value of voltage and one value of current in temporary memory wile them transferred through the parallel port using a software written in C#.

The parallel port able us to transfer a 8 bit  we give 5 bit for the voltage (max voltage 22v) and 3 bit for the current (max current 3.4 A).

After all the value ordered in table in the interface which written in C# also and then the interface do his job including the drawing the characteristics and calculate the values which needed (look interface chapter).

Commercial capture
here we just show the I-V tester  ready to sell by WACOM Electric CO  the tester is available in different modules depend on the range of voltage and current.

And here is the software which provided with the model

The power electronic circuit & the sensor

The power electronic circuit of this device consists of capacitors, resistors, special resistors and switches as shown in the figure below

1)the capacitors is chosen up to measure a cell have a rated 22 open circuit voltage and 3.5 short-circuit current and from equation in chapter 3 we use 14 mF capacitors bank consist of 5 capacitors

2) The switches here can be relays or transistors of ordinary switches (pushbutton)

3) RL is 10 KΩ and that to protect the capacitors from the reverse current

4) Rshunt is an special resistor its convert the current which follow in it to mV in constant ratio

The sequence of measuring:

Before of all we must close switch 3 to rest the capacitors form any charge they may contain then we open switch 3 and close switch 1 to start the charging of capacitors in time constant determined by the capacitors and during this operation we measure the open circuit voltage after we reduce it by constant factor using potentiometer by the inputs leg of the pic to the ADC then in 8 bit though the parallel port to the software.

When the capacitor become fully charged we short the cell using switch 2 to measure the short circuit current using Rshunt which convert the amperes in mile volts to transfer it through the PIC and parallel port as the voltage transferred.

Also we need form this circuit the radiation and the temperature of the cell and the ambient.

To measure the temperatures we use a sensor (LM355) and cable to enter the data to the software directly as the following equation:

Tamb=25V/ 2.982

To measure the radiation we make an equivalent sensor consists of thin film cell  with an adapter consists of two terminals and a resistor 100Ω 1 watt
We test this cell by comparing its reading in volts to the reading of solar meter and we find that the relation is liner in this equation:

G= 227.6V- 69.62

Where V is the reading of the cell which will be transferred to the software in the same way that the opencircuit voltage was transferred

And now all the data is transferred to the enter face and ready to be calculated and the drawn

the inter face and The PIC circuit

The PIC circuit

The sequence of work

The Code

The code was written in C# language:

using System;

using System.Collections.Generic;

using System.ComponentModel;

using System.Data;

using System.Drawing;

using System.Text;

using System.Windows.Forms;

using ZedGraph;

using System.Threading;

using System.Runtime.InteropServices;

using System.Collections;

namespace pvChar

{

public partial class Form1 : Form

{

public bool read = false;

double maxPow=0;

double maxVol=0;

double maxCur=0;

// another values"

double Voc;

double Isc;

double Pm;

double Vmpp;

double Impp;

double nMax;

double G;

double Tamp;

double Tcell;

double fillFactor;

//max power coordinates:

double maxPowerX = 0;

double maxPowerY = 0;

//lpt variabels:

public Thread th;

//   public Thread th;

[DllImport("lpt.dll")]

static extern void writeLpt(short data);

[DllImport("io.dll")]

static extern void PortOut(short Port, char Data);

[DllImport("io.dll")]

static extern char PortIn(int Port);

[DllImport("io.dll")]

static extern void PortWordOut(short Port, int Data);

/// <summary>

///

/// </summary>

int rowCounter = 0;

public GraphPane gp;

public Form1()

{

InitializeComponent();

}

public void polling()

{

int tableCount = 0;

char intRec;

// int tmp;

string voltage, current, radiation;

double rad=0;

//byte []tmp= new byte[4];

//byte[] tmp2 = new byte[4];

char[] buffer = new char[16];

buffer = new char[16];

Thread.Sleep(1000);

while(read)

{

//read voltage and show it

serialPort1.Write("a");

Thread.Sleep(500);

serialPort1.Read(buffer,0,4);

voltage = new string(buffer);

dataGridView1[0, 0].Value = double.Parse(voltage) * 4.694;//voltage factor

//MessageBox.Show("hello");

//read current and show it

serialPort1.Write("a");

Thread.Sleep(500);

serialPort1.Read(buffer,0,4);

current = new string(buffer);

dataGridView1[1, 0].Value = double.Parse(current) / 0.5;

//calculate the power and show it

dataGridView1[2, 0].Value = double.Parse(current.ToString()) * double.Parse(voltage);

//read radiation and show it

serialPort1.Write("a");

//MessageBox.Show(serialPort1.ReadBufferSize.ToString());

Thread.Sleep(500);

serialPort1.Read(buffer, 0, 4);

radiation = new string(buffer);

// MessageBox.Show(radiation);

rad = double.Parse(radiation);

rad = rad * 227.6 - 69.62;

gTXT.Text = rad.ToString();

//MessageBox.Show("hello");

// dataGridView1.RowCount++;

dataGridView1.Rows.Insert(0, 1);

// Thread.Sleep(500);

}

// th.Suspend();

// MessageBox.Show(st);

//   result.Text = ((int)intRec).ToString();

// while (true)

// {

//   //  while (receive() == intRec) ;

//     timer1.Start();

//     intRec = receive();

//     byte current = (byte)intRec;

//     current&=0x0F;

//     //current is ready

//     byte voltage= (byte) intRec;

//     voltage&=0xF0;

//     voltage >>= voltage;

//     voltage >>= voltage;

//     voltage >>= voltage;

//     voltage >>= voltage;

//     double voltValu = double.Parse(voltage.ToString());

//     double curValu = double.Parse(current.ToString());

//     double powValu = double.Parse(current.ToString()) * double.Parse(voltage.ToString());

//     if (curValu > maxCur) maxCur = curValu;

//     if (voltValu > maxVol) maxVol = voltValu;

//     if (powValu > maxPow) maxPow = powValu;

//     //current and voltage done, plot it yaba:

//     dataGridView1[0, tableCount].Value = double.Parse(current.ToString());

//     dataGridView1[1, tableCount].Value = double.Parse(voltage.ToString());

//     dataGridView1[2,tableCount++].Value= double.Parse(current.ToString()) * double.Parse(voltage.ToString());

////     result.Text = ((int)intRec).ToString();

// }

}

public char receive()

{

PortOut(0x37A, (char)0x21);

char st1 = PortIn(0x378);

return st1;

}

private void Form1_Load(object sender, EventArgs e)

{

try

{

gp = zedGraphControl1.GraphPane;

gp.XAxis.MajorGrid.IsVisible = true;

gp.YAxis.MajorGrid.IsVisible = true;

gp.XAxis.MajorGrid.Color = Color.LightGray;

gp.YAxis.MajorGrid.Color = Color.LightGray;

gp.XAxis.Title.Text = "Voltage";

gp.YAxis.Title.Text = "Current";

gp.Title.Text = "IV Charactaristic";

th = new Thread(new ThreadStart(polling));

timer1.Interval = int.Parse(samplIntrTxt.Text);

}

catch (Exception exp)

{

MessageBox.Show(exp.Message);

}

}

private void button2_Click(object sender, EventArgs e)

{

//    GraphPane gp= zedGraphControl1.GraphPane;

//    PointPairList l1 = new PointPairList();

//    double x, y1, y2;

//    for (int i = 0; i < 36; i++)

//    {

//        x = (double)i + 5;

//        y1 = 1.5 + Math.Sin((double)i * 0.2);

//        y2 = 3.0 * (1.5 + Math.Sin((double)i * 0.2));

//        l1.Add(x, y1);

//    }

//LineItem li= gp.AddCurve("test", l1, Color.Red, SymbolType.Circle);

//gp.AxisChange();

}

private void button1_Click(object sender, EventArgs e)

{

int row = 0;

//read  rows/cols values:

PointPairList l1 = new PointPairList();

PointPairList operationSquare = new PointPairList();

double x, y;

// MessageBox.Show(dataGridView1.RowCount.ToString());

maxCur = 0;

maxVol = 0;

maxPow = 0;

for (row = 1; row < dataGridView1.RowCount; row++)

{

//  try

{

x = double.Parse(dataGridView1[0, row].Value.ToString());

if (x > maxVol) maxVol = x;

y = double.Parse(dataGridView1[1, row].Value.ToString());

if (y > maxCur) maxCur = y;

//  dataGridView1[2, row].Value = x * y;

if (x * y > maxPow)

{

maxPow = x * y;

maxPowerX = x;

maxPowerY = y;

}

l1.Add(x, y);

}

//catch (Exception exp)

//{

//    MessageBox.Show(exp.Message + exp.Source);

//}

}

//   MessageBox.Show("maxVol:" + maxVol.ToString() + "  maxCur: " + maxCur.ToString()

//       +" maxPower: " + maxPow.ToString());

calculateValues();

LineItem li = gp.AddCurve("I-V Characteristics", l1, Color.Blue, SymbolType.Diamond);

// li.Line.Fill = new Fill(Color.Blue);

// plot opSquare:

operationSquare.Add(0, maxPowerY);

operationSquare.Add(maxPowerX, maxPowerY);

operationSquare.Add(maxPowerX, 0);

LineItem opSquare = gp.AddCurve("OperationSquare", operationSquare, Color.Red, SymbolType.None);

opSquare.Line.Fill = new Fill(Color.Goldenrod);

gp.Legend.Position = ZedGraph.LegendPos.Bottom;

gp.AxisChange();

//     gp.AxisChange();

dateLbl.Text = System.DateTime.Now.Day.ToString() + "/" + System.DateTime.Now.Month.ToString() + "/" + System.DateTime.Now.Year.ToString();

timeLbl.Text = System.DateTime.Now.Hour.ToString() + ":" + System.DateTime.Now.Minute.ToString() + ":" + System.DateTime.Now.Second.ToString();

}

public void calculateValues()

{

//1) calculate Voc

try

{

Voc = maxVol;

Isc = maxCur;

Pm = maxPow;

Vmpp = maxPowerX;

Impp = maxPowerY;

fillFactor = (Vmpp * Impp) / (Voc * Isc);

G = double.Parse(gTXT.Text);

nMax = Pm / (G * double.Parse(cellAreaTxt.Text));

VocLbl.Text = Voc.ToString();

iscLbl.Text = Isc.ToString();

pmLbl.Text = Pm.ToString();

vmppLbl.Text = Vmpp.ToString();

imppLbl.Text = Impp.ToString();

fillFactorLbl.Text = (Math.Round(fillFactor, 4)*100).ToString()+" %";

nMaxLbl.Text = (nMax*100).ToString()+ " %";

}

catch (Exception exp)

{

MessageBox.Show("Verify your input Values, " + exp.Message);

}

}

private void dataGridView1_RowEnter(object sender, DataGridViewCellEventArgs e)

{

}

private void dataGridView1_RowLeave(object sender, DataGridViewCellEventArgs e)

{

try

{

dataGridView1[2, rowCounter].Value =

double.Parse(dataGridView1[0, rowCounter].Value.ToString()) *

double.Parse(dataGridView1[1, rowCounter].Value.ToString());

rowCounter++;

}

catch (Exception)

{

}

}

private void startReadBtn_Click(object sender, EventArgs e)

{

if (startReadBtn.Text == "Start Reading")

{

read = true;

//th = new Thread(new ThreadStart(polling));

//timer1.Interval = int.Parse(samplIntrTxt.Text);

startReadBtn.Text = "Stop Reading";

//if (th.IsAlive)

//{

//    th.Abort();

//    th = new Thread(new ThreadStart(polling));

//}

if (th.ThreadState == ThreadState.Suspended)

{

th.Resume();

}

else th.Start();

}

else

{

startReadBtn.Text = "Start Reading";

read = false;

th.Suspend();

}

}

private void button2_Click_1(object sender, EventArgs e)

{

timer1.Interval = int.Parse(samplIntrTxt.Text);

}

private void zedGraphControl1_Load(object sender, EventArgs e)

{

}

private void button3_Click(object sender, EventArgs e)

{

}

private void serialBtn_Click(object sender, EventArgs e)

{

try

{

serialPort1.PortName = serialNameCombo.Text;

serialPort1.Open();

startReadBtn.Enabled = true;

}

catch (Exception exp)

{

MessageBox.Show(exp.Message);

}

}

private void button3_Click_1(object sender, EventArgs e)

{

byte[] t1;

string s = "1.02";

t1= ASCIIEncoding.ASCII.GetBytes(s);

string s2 = ASCIIEncoding.ASCII.GetString(t1);

MessageBox.Show(s2);

}

private void zedGraphControl1_Load_1(object sender, EventArgs e)

{

}

private void groupBox3_Enter(object sender, EventArgs e)

{

}

private void Form1_FormClosing(object sender, FormClosingEventArgs e)

{

try

{

if (th.ThreadState == ThreadState.Suspended)

{

th.Resume();

}

th.Abort();

}

catch { };

}

}

}

The PIC circuit

The function of the PIC in our project is to convert the input data from the circuit form analog to digital using the built in ADC in it and we use it also as an bridge between the circuit and the parallel port

If we want to advance the project and convert the push button to an automatic switch we can add an ATS (automatic transfer switch) software and by using this we can control the switches automatically  

In this project we faced a problem which represented in how to scale the voltage which come  from the terminals of the cell and the terminals of the special resistor 
The voltage which come from the terminals is varied from 0 to 23 V and the PIC just receive from 0 to 5 V and to do that we use a simple voltage divider circuit (100Ω and 27Ω) and from the 27Ω resistor and then in the interface we multiply by 4.6938

And for the resistor which give us a range from 0 to 100mV we use an OPAMP 741 with two resistors to construct a non inverting amplifier with a factor  50

ALSO to convert from analog to digital we use the built in ADC in the PIC but we still need a PIC/C++ CODE which is below

//#include <LCD.C>

#include <float.h>

//#use fast_io(b)

float value;

float readValue;

int count,ch;

int flag;

float  result, avg;

int16 sb;

void main()

{

setup_adc_ports(ALL_ANALOG);

setup_adc(ADC_CLOCK_INTERNAL);

setup_psp(PSP_DISABLED);

setup_spi(FALSE);

setup_timer_0(RTCC_INTERNAL|RTCC_DIV_1);

setup_timer_1(T1_DISABLED);

setup_timer_2(T2_DISABLED,0,1);

//();

// TODO: USER CODE!!

readvalue=0;

count=0;

value=0;

ch=0;

flag=0;

result=0;

avg=0;

//  printf("hello");

//while(!kbhit()){

//   delay_us(1);

//}

//   sb= getchar();

//   if(&sb== 'y')

//{

while(1)

{

while(!kbhit()){

delay_us(1);

}

sb= getchar();

restart_wdt();

flag=1;

result=0;

avg=0;

readValue=0;

delay_ms(200);

//if(!input(PIN_B0))

if(1)

{

ch++;

if(ch==4)

ch=1;

}

if(ch==1 )

{

set_adc_channel (0);

for( count=0; count<4; count++)

{

restart_wdt();

readValue+= read_adc();

delay_ms(50);

restart_wdt();

}

flag=0;

restart_wdt();

avg= readValue/4;

result= (avg *5)/1023;

printf("%f", result);

//printf(LCD_PUTC, "\f");

//printf(LCD_PUTC, "ch.1= %f",result);

}

else if(ch==2  )

{

set_adc_channel (1);

for( count=0; count<4; count++)

{

restart_wdt();

readValue+= read_adc();

delay_ms(50);

restart_wdt();

}

flag=0;

restart_wdt();

avg= readValue/4;

result= (avg *5)/1023;

printf("%f", result);

//printf(LCD_PUTC, "\f");

// printf(LCD_PUTC, "ch.2= %f",result);

}

else if(ch==3 )

{

set_adc_channel (2);

for( count=0; count<4; count++)

{

restart_wdt();

readValue+= read_adc();

delay_ms(50);

restart_wdt();

}

flag=0;

restart_wdt();

avg= readValue/4;

result= (avg *5)/1023;

printf("%f", result);

//printf(LCD_PUTC, "\f");

// printf(LCD_PUTC, "ch.3= %f",result);

}

restart_wdt();

}

}

//}

pictures showing the project

Chapter Five

TEST example

We did the test on a PV MODULE from the energy research center of An-Najah national university

The specifications of the MODULE:

SEMENIS M53
V O.C = 21.5 v                    I S.C = 3.4 A         POWER = 53 watt

| 0 | 3.45 | 0 |
| --- | --- | --- |
| 3.45 | 3.45 | 1 |
| 6.9 | 3.45 | 2 |
| 10.35 | 3.45 | 3 |
| 13.8 | 3.45 | 4 |
| 17.25 | 3.45 | 5 |
| 20.7 | 3.45 | 6 |
| 24.15 | 3.45 | 7 |
| 27.6 | 3.45 | 8 |
| 31.05 | 3.45 | 9 |
| 34.5 | 3.45 | 10 |
| 37.95 | 3.45 | 11 |
| 40.02 | 3.45 | 11.6 |
| 45.195 | 3.45 | 13.1 |
| 48.99 | 3.45 | 14.2 |
| 49.538 | 3.4 | 14.57 |
| 50.82 | 3.3 | 15.04 |
| 49.1667 | 3.17 | 15.51 |
| 44.828 | 2.8 | 16.01 |
| 41.325 | 2.5 | 16.53 |
| 37.444 | 2.2 | 17.02 |
| 31.554 | 1.8 | 17.53 |
| 26.1435 | 1.45 | 18.03 |
| 18.52 | 1 | 18.52 |
| 10.45 | 0.55 | 19 |
| 0 | 0 | 19.5 |

Chapter Six

Alternating method

Measuring Photovoltaic Cell I-V Characteristics

with the Model 2420 SourceMeter Instrument

Introduction

Photovoltaic (PV) cells convert sunlight directly to electricity. Fabricated from a wide variety of materials using many different processing techniques, these devices are used for terrestrial power generation, as well as commercial, military, and research space power applications. PV cell characterization involves measuring the cell’s electrical performance characteristics to determine conversion efficiency and critical equivalent circuit parameters. It is an important tool for R&D and production of cells and photovoltaic arrays. This application note describes how to use the Keithley Model 2420 High Current SourceMeter®

instrument to measure the current-voltage (I-V) characteristicsof PV cells.

With the introduction of SMUs (Source-Measure Units),configuring device characterization systems that once required arack of electronic equipment, including programmable power supplies, digital multimeters, and scanners, has been simplified significantly. The Model 2420’s ability to source/sink up to 3A

with 0.5% accuracy or better and its low noise, high impedance, repeatable DMM offers a cost-effective alternative to using expensive, high power programmable power supplies for PV cell characterization. The Model 2420 offers 10μV resolution on the 2V range, which is sufficient to measure the I-V curve of any

single junction cell. The 20V range offers adequate resolution (100μV) for multi-junction cells and small arrays, where the open circuit voltage may exceed 2V. The Model 2420’s low current measuring capability, with 10pA maximum resolution on the 1mA current range, is sufficient for virtually all dark I-V

applications

Test Description

A PV cell may be represented by the equivalent circuit model shown, consisting of a photon current source (IL), a diode, a series resistance (rs), and a shunt resistance (rsh).

The series resistance (rs) represents the ohmic losses in the front surface of the cell and the shunt resistance (rsh) represents the loss due to diode leakage currents. The conversion efficiency  is defined as:

where Pin is the power input to the cell, Voc is the open circuit voltage, Isc is the short circuit current, and Im and Vm are the maximum cell current and voltage respectively at the maximum power point, Pm = ImVm. Figure 2 illustrates the typical I-V characteristics of an Si PV cell, showing Im and Vm at the maximum

power point.

Critical PV cell performance parameters, such as the equivalent cell shunt and series resistance and the electrical conversion efficiency and fill factor, may be determined from I-V measurements. The cell must be maintained at a constant temperature and a radiant source with a constant intensity and a known

spectral distribution must be used.

Forward Bias I-V (Illuminated)

This test involves generating the forward biased I-V curve between the two points (V1 = 0, I1 = Isc ) and (V2 = Voc, I2 = 0). The parameters Voc and Isc can be directly determined from the curve and Im, Vm, Pm, FF, and are easily calculated. Additionalanalytical techniques may be used to determine rs and rsh.

Reverse Bias I-V (Dark)

The reverse bias I-V curve test is performed in the dark between 0V and the level where breakdown begins to occur. In this region, the slope of the current-voltage characteristic can be used to estimate the shunt resistance (rsh).

Test System and Configuration

Figure 3 illustrates the measurement configuration for generating the illuminated forward bias I-V characteristics, using a Model 2420 and a 4-wire connection to the cell to minimize measurement lead resistance errors. A solar simulator provides appropriate illumination for the cell and a cooled, vacuum hold own chuck secures the cell and provides isothermal test conditions.

The series resistance (rs) of a PV cell is low, typically <1ohmfor cells designed for operation at 1 sun and <0.1ohmfor concentratorcells. As a result, direct contact to the cell bus bar with specially designed 2-point probes is essential to obtain accurate

Figure 4 is a schematic of a measurement configuration to generate the dark reverse I-V characteristics. If the dark reverse currents to be measured are >1μA, the unguarded 4-wire configuration will provide accurate measurements. For dark reverse currents <1μA, stray leakage currents in cables and fixturing

may create errors and noise in measurements. Two methods can be used to reduce or eliminate these sources of error. The first requires using high resistance materials when constructing the test fixture and keeping the fixture free of contaminants. The second method employs the Model 2420’s built-in guard

circuitry. In Figure 4, the V-guard output of the Model 2420 is a low impedance source at nearly the same potential as the high impedance point, HI (output). Guarding is used in this circuit to ensure the contact probe housing remains isolated from the circuit. The probe housing is constructed from insulating

materials; however, contamination may cause a breakdown in resistance and introduce measurable stray currents. The guard plate under the probe, at approximately the same potential as the probe on the top contact of the cell, ensures no current can flow through the probe housing, so the current measured flows

through the cell. forward bias I-V measurements

Programming the 2420 forCell Characterization

Any of the example programs on Keithley’s web site that carry out an I-V sweep would be an excellent starting point. Examplesare available in a number of programming languages at www.keithley.com. Our LabTracer application is an additional software source. LabTracer was developed in Test Point but is provided as a runtime. Therefore, Test Point is not required to run LabTracer.

Equipment List

The following equipment is required to assemble a PV cell characterization

system:

1. Keithley Model 2420 SourceMeter instrument

2. IEEE-488 interface such as the Keithley KPCI-488

3. Source illumination (solar simulator)

4. Temperature-controlled hold down chuck/test fixture

5. Keithley 7007-x IEEE-488 Interface cable

6. Test leads (4-wire) and 2-point adjustable contact probe(s)

References 

1)Marwan  M. Mahmoud, Transient analysis of a PV power generator charging

a capacitor for measurement of the I–V characteristics , Energy Research Centre, An Najah National University,

2)Santi Wangnipparnto, The development of IV CURVE tester for photovoltaic model

Electrical Engineering department, Pathumwan Institute of Technology, Bangkok,10330

3) Keithley Instruments, Inc. Measuring Photovoltaic Cell I-V Characteristics

with the Model 2420 SourceMeter Instrument

4) K. Bouzidi, M. Chegaar, Solar cells parameters evaluation considering the series and shunt resistance, Physics Department, Ferhat Abbas University

Contents

Chapter One:Introduction	4

Chapter Two:Photovoltaic Cells	7

Photovoltaic Cells.	8

Polycrystalline silicon	9

Ribbon silicon	9

Amorphous or thin film silicon	10

Photovoltaic Modules	10

Summary of Current Photovoltaic Technology	11

Describing Photovoltaic Module Performance.	11

Photovoltaic Arrays.	15

Chapter Three:Transient analysis of a PV power generator charging a capacitor for measurement of the I–V characteristics	18

The power electronic circuit	19

Chapter Four :The project	22

The Block diagram of  Project:	23

Commercial capture	24

The power electronic circuit & the sensor	25

the inter face and The PIC circuit	26

The sequence of work	28

The Code	29

Chapter Five:TEST example	47

Chapter Six : Alternating method	50

Measuring Photovoltaic Cell I-V Characteristics	51

with the Model 2420 SourceMeter Instrument	51

Introduction	51

Test Description	52

Forward Bias I-V (Illuminated)	53

Reverse Bias I-V (Dark)	53

Test System and Configuration	54

Programming the 2420 forCell Characterization	55

Equipment List	55

References	56

# Text boxes

Draw the data and auto scale it and fill the square operation

Determining the sample time interval and start importing from parallel port

Calculate the fill factor and the efficiency

Arrange the data in the table ,find the max power ,Voc, Isc,Vmpp,  Impp and the radiation and T’s

2009

V               I               P