## Slide 1: Optimal Design, Simulation and Testing of Grid Connected PV Power Systems for Selected Daily Energy Loads
Submitted to:
Prof. Dr. Marwan Mahmoud
Prepared By:
Islam Sonono11316522
May Al Mashni 11314830
Ghazal Hanani 11316129

## Slide 2: Contents
20 Kwp designing and simulation.
Real case study of designing a PV system for the engineering faculty building.
Economical study for both.

## Slide 3: 20 Kwp designing and simulation
The PV-modules :
Module serial code : Hanwha_Qcells_QPLUS_L-G4_2_335.
Module Watts STC : 335 Watts.
Max power voltage (Vmpp) : 37.33 Volts.
Max power current (Impp) : 8.97 Amps.
Open circuit voltage (Voc) : 46.81 Volts.
Short circuit currents (Isc) : 9.54 Amps.
Module efficiency : 16.80%.

## Slide 4: 20 Kwp designing and simulation
Two scenarios :
Using one inverter 20 kw.
Using two inverters 10 kw.

## Slide 5: 20 Kwp designing and simulation
Using one inverter 20 kw.
Inverter code : TRIO_20_0_0_OUTD_S1_US
Absolute Max.DC voltage : 1000 Volts
Nominal power : 20 KW
Maximum efficiency : 97.3%
Number of MPPT : 2
Max. Ac output current : 33 Amps
Technology : three-phase

## Slide 6: 20 Kwp designing and simulation Using one inverter 20 kw.

## Slide 7: 20 Kwp designing and simulation
Using two inverters 10 kw.
Inverter code : PVI-10.0-TL-OUTD
Absolute Max.DC voltage : 900 Volts
Nominal power : 10 KW
Maximum efficiency : 97.8%
Number of MPPT : 2
Max. Ac output current : 16.6 Amps
Technology : three-phase

## Slide 8: 20 Kwp designing and simulation Using two inverters 10 kw.

## Slide 9: Shading on PV systems and spacing between rows
Parameters:
The distance equation:

## Slide 10: self-shading calculations using PVsys simulation
Number of sheds: 2 (2 strings each contains 2 combined rows).
Collector band width: 2 m.
Top inactive band : 10 cm
Pitch (self-distance between 2 rows): 4 m (it was calculated in the previous part).
Plan tilt: 30.
Azimuth : 0.

## Slide 11: Graph shows the loss factor values under several conditions

## Slide 12: 20 Kwp designing and simulation

## Slide 13: Real case study of designing a PV system for the engineering faculty building

## Slide 14: Real case study of designing a PV system for the engineering faculty building
Orientations and geographical location of the building :

## Slide 15: Real case study of designing a PV system for the engineering faculty building
Two scenarios :
1. The azimuth angle is 10 and the available area is totally selected.
2. The azimuth angle is 0 and the system is exactly facing south.

## Slide 16: First scenario for 10 azimuth and larger roof top area

## Slide 17: First scenario for 10 azimuth and larger roof top area
Q Plus L-G4.2 335, 335 w 31 V Inverter 60 kw SMA

## Slide 18: First scenario for 10 azimuth and larger roof top area

## Slide 19: First scenario for 10 azimuth and larger roof top area

## Slide 20: First scenario for 10 azimuth and larger roof top area
System Simulation and Results using PVsys

## Slide 21: First scenario for 10 azimuth and larger roof top area

## Slide 22: First scenario is the 0 azimuth and the system is exactly facing south
Q Plus L-G4.2 335, 335 w 31 V Inverter 25 kw SMA

## Slide 23: First scenario is the 0 azimuth and the system is exactly facing south

## Slide 24: Second scenario is the 0 azimuth and the system is exactly facing south

## Slide 25: First scenario is the 0 azimuth and the system is exactly facing south
System Simulation and Results using PVsys

## Slide 26: First scenario is the 0 azimuth and the system is exactly facing south

## Slide 27: Economical study
For 20kwp system :
a. case 1: using one inverter 20 kw.
b. case 2: using two inverters 10 kw.
Real study
a. case 1: in azimuth zero.
b. case 2: in azimuth ten.

## Slide 28: Economical study for 20 kwp system using one inverter
Initial investment = 85364NIS
Depreciation factor for the system = 1 %.
Assume selling cost for 1 KWh = 0.6 NIS.
Life time cycle for the system = 25 years.
Energy gained from the system = 36578 KWh.
Saving from the system = 21946.8 NIS.
Margin of profits + Initial investment=114000 NIS.
Maintenance cost = 1.5% * total initial cost =0.015*114 000=1710NIS/year.
Inverter cost=10900 NIS.
Cost (NIS) | Type of cost ( for using one inverter )
650 | Cable cost
6504 | Protection element cost
78210 | Other element cost
85364 | Total

## Slide 29: Economical study for 20 kwp system using one inverter
P.P.B
NIS/year.
NIS/year.

## Slide 30: Economical study for 20 kwp system using one inverter
P.P.B
A = 19660.956 NIS/year.
NIS/year.
114000NIS

## Slide 31: Economical study for 20 kwp system using two inverters
Initial investment = 88394 NIS
Depreciation factor for the system = 1 %.
Assume selling cost for 1 KWh = 0.6 NIS.
Life time cycle for the system = 25 years.
Energy gained from the system = 36578 KWh.
Saving from the system = 21946.8 NIS.
Inverter cost =13000 NIS.
margin of profits + Initial investment=118000 NIS.
Maintenance cost = 1.5% * total initial cost=1770NIS/year.
Cost (NIS) | Type of cost ( for using TWO inverters)
405 | Cable cost
7679 | Protection element cost
80310 | Other element cost
88394 | Total

## Slide 32: P.P.B
Economical study for 20 kwp system using two inverters
A=20024.6 NIS/year.
A=NIS/year.

## Slide 33: Economical study for 20 kwp system using two inverters
P.P.B
A = 20400.475 NIS/year.
NIS/year

## Slide 34: Economical study for 20 kwp system
In the case 2 : The cost of 1 wp = 1.55 $/wp
Case2(10kwp inverter) | Case 1(20kwp inverter) | Case
6.34 | 6.127 | Ideal case
 | 6.23 | Inverter case
Case2(10kwp inverter) | Case 1(20kwp inverter) | Case
6.34 | 6.127 | Ideal case
 | 6.23 | Inverter case
Recommended :

## Slide 35: Economical study for real study (in azimuth zero)
Initial investment = 406611 NIS
Depreciation factor for the system = 1 %.
Assume selling cost for 1 KWh = 0.6 NIS.
Life time cycle for the system = 25 years.
Energy gained from the system = 186500KWh.
Saving from the system = 111900NIS
Cost of one inverter = 15000 NIS.
margin of profits + Initial investment=550000 NIS.
Maintenance cost = 1.5% * total initial cost =0.015*118000=8250NIS/year.
Cost (NIS) | Type of cost (in azimuth zero)
2380 | Cable cost
22321 | Protection element cost
381910 | Other element cost
406611 | Total

## Slide 36: Economical study for real study (in azimuth zero)
P.P.B
A = 93335 NIS/year.
NIS/year.

## Slide 37: Economical study for real study (in azimuth zero)
P.P.B
A = 93905.378 NIS/year.
NIS/year.

## Slide 38: Economical study for real study (in azimuth 10)
Initial investment = 454774NIS..
Depreciation factor for the system = 1 %.
Assume selling cost for 1 KWh = 0.6 NIS.
Life time cycle for the system = 25 years.
Energy gained from the system = 220700 KWh.
Saving from the system = 132420NIS.
Inverter cost =25000NIS
margin of profits + Initial investment=680000 NIS.
Maintenance cost = 1.5% * total initial cost = 10200 NIS/year
Cost (NIS) | Type of cost (in azimuth zero)
3090 | Cable cost
21374 | Protection element cost
422310 | Other element cost
454774 | Total

## Slide 39: Economical study for real study (in azimuth 10)
P.P.B
A = 115396 NIS/year
A NIS/year.

## Slide 40: Economical study for real study (in azimuth 10)
P.P.B
A =115871.3 NIS/year.
NIS/year.

## Slide 41: Economical study for real study
Case | Ideal case P.P.B (years) | Worse case P.P.B (years) | Energy/years (Kw/years) | cost for 1wp ($)
100kwp | 5.7976 | 5.833 | 119000 | 1.4
120kwp | 6.057 | 6.08 | 220700 | 1.4
Recommended :

## Slide 42: Conclusions
The 20 Kwp project we choose the case with two 10 kw inverter rather than one 20 kw inverter because of reliability issues , and for the Engineering and Information technology building project we have chosen the case where the azimuth angle is 10 degree rather than 0 because in this case we can maximize the area we have on the roof top so we can put more modules and produce more energy up to 120 KWp rather than 100 KWp in the 0 degree azimuth , and for the optimum working hours it will differ in timing through the day but in total it will remain the same.

## Slide 43
Any questions ?