## Slide 1: An Experimental Comparison between Monofacial and Bifacial PV Modules under different Conditions
Students:
Mahmoud Kobari
Ahmad Mallak
Ahmad Titi
Supervisor:
Dr. Adel Juaidi
1

## Slide 2: Our Project
Comparison between Monofacial and Bifacial PV Modules under different Conditions
2

## Slide 3: Solar Energy
Renewable
Green
Two SDGs Goals
3

## Slide 4: Fossil fuel Solar energy
Palestine solar energy installed capacity approx. 130 MW
Palestine relies on Israeli occupation for 100% of its fossil fuel imports
Energy In Palestine
Electricity
Palestine are highly dependent on
electricity provided by the IEC,
around 93.4% of total consumption
4

## Slide 5: Monofacial vs. Bifacial
5

## Slide 6: Monofacial vs. Bifacial
6

## Slide 7: Monofacial vs. Bifacial
Low albedo sensitivity
High albedo sensitivity
01
02
01
02
High temperature
Low temperature
03
03
High ability
to absorb the irradiance
Low ability
to absorb the irradiance
7

## Slide 8: Methodology
 Surface Change
 Orientation Change
Project 1
Project 2
Engineering faculty PV System  Surface Change
Four PV Module
By PVsyst software
8

## Slide 9: Engineering faculty PV System
9

## Slide 10: Albedo
Black Asphalt
Artificial Green Grass
Sand
White Paint
0.12
0.26
0.35
0.90
10

## Slide 11: PVsyst Software
Geographical Data
Orientation
System Selection
Shading Analysis
11

## Slide 12: Geographical Data
PV GIS
Orientation
Tilt Angle=28°
Building Azimuth Angle =11.6°
Latitude
Longitude
V.2
32.23 °N
35.22 °E
12

## Slide 13: System Selection
System Capacity
Monofacial
Bifacial
72.8 KW
Q.POWER-325W
Jinko-325W
13

## Slide 14: Shading Analysis
14

## Slide 15
RESULTS
15

## Slide 16: Energy Production
Monofacial
Material Type | Albedo (%) | Produced Energy (kWh/year) | Specific Production (kWh/kWp/year)
Black Asphalt | 0.12 | 142,182 | 1870
Artificial Green Grass | 0.26 | 142,820 | 1878
Sand | 0.35 | 143,230 | 1883
White Paint | 0.90 | 145,719 | 1916
Bifacial
Material Type | Albedo (%) | Produced Energy (kWh/year) | Specific Production (kWh/kWp/year)
Black Asphalt | 0.12 | 132,877 | 1825
Artificial Green Grass | 0.26 | 133,463 | 1833
Sand | 0.35 | 133,839 | 1838
White Paint | 0.90 | 136,122 | 1870
16

## Slide 17: sun path curve (Iso-shadings diagram)
17

## Slide 18: Production, gains and losses curves albedo 0.9
Monofacial
Bifacial
18

## Slide 19: Production, gains and losses curves albedo 0.9
Monofacial
Bifacial
19

## Slide 20: Gain Factors
Monofacial
Bifacial
Material Type | Albedo (%) | The global incident in coll. plane | Module Quality
Black Asphalt | 0.12 | +10.5% | +0.37
Artificial Green Grass | 0.26 | +11.3% | +0.37
Sand | 0.35 | +11.8% | +0.37
White Paint | 0.90 | +15.0% | +0.37
Material Type | Albedo (%) | The global incident in coll. plane | Module Quality
Black Asphalt | 0.12 | +10.5% | +0.75
Artificial Green Grass | 0.26 | +11.3% | +0.75
Sand | 0.35 | +11.8% | +0.75
White Paint | 0.90 | +15.0% | +0.75
20

## Slide 21: Losses Factors
Monofacial
Bifacial
Material Type | Albedo %)) | Near Shadings: irradiance loss | IAM factor on global | PV loss due to irradiance level | PV loss due to temperature | Mismatch loss, modules and strings | Ohmic wiring loss | Inverter Loss
Black Asphalt | 0.12 | -0.90% | -2.00% | -0.35% | -10.87% | -2.15% | -1.25% | -2.38%
Artificial Green Grass | 0.26 | -1.08% | -2.04% | -0.35% | -10.93% | -2.15% | -1.26% | -2.38%
Sand | 0.35 | -1.20% | -2.06% | -0.35% | -10.97% | -2.15% | -1.27% | -2.38%
White Paint | 0.90 | -1.89% | -2.19% | -0.35% | -11.21% | -2.15% | -1.29% | -2.40%
Material Type | Albedo (%) | Near Shadings: irradiance loss | IAM factor on global | PV loss due to irradiance level | PV loss due to temperature | Mismatch loss, modules and strings | Ohmic wiring loss | Inverter Loss
Black Asphalt | 0.12 | -0.90% | -1.75% | -0.42% | -9.28% | -2.15% | -1.23% | -2.31%
Artificial Green Grass | 0.26 | -1.08% | -1.79% | -0.42% | -9.33% | -2.15% | -1.24% | -2.31%
Sand | 0.35 | -1.20% | -1.81% | -0.41% | -9.36% | -2.15% | -1.25% | -2.33%
White Paint | 0.90 | -1.89% | -1.96% | -0.41% | -9.56% | -2.15% | -1.27% | -2.32%
21

## Slide 22
The bifacial module consistently outperforms the monofacial module, with an average increase of 6.81% in energy production and higher specific production
22

## Slide 23
THANKS