## Slide 1: Design of a wastewater collection network of Madama Village By Hayat Al-fares (11715536) Ro'a Ataya (11716272) Under Supervision of: Dr. Mohammad N. Almasri

## Slide 2: OUTLINE Introduction Design of a wastewater collection network 02 01 Cost of the Network 03 04 Recommendations

## Slide 3: 01 INTRODUCTION 1. Background 2. Objectives 3. Methodology

## Slide 4: Background

## Slide 5: About Madama
Madama is a Palestinian Village located in the West Bank. It is located about 5 Km south of Nablus. have an elevation of 498 meters above sea level and Its area is approximately 3,400 dunums.
According to the Municibility data, the total population in Madama Village about 2,239 capita in 2021.
Location of Madama Village

## Slide 6: Objectives
Design of a wastewater collection network of Madama Village using SewerCAD
Estimate the cost of the network
Suggest a suitable wastewater treatment plant location.

## Slide 7: Methodology
Data analysis and assessment using Excel
Selection of the project idea
Selection of the study area
Data collection
Construction of WWCN using sewerCAD
Design of the WWCN hydraulically
Cost estimation
Recommendations

## Slide 8: Design of a Wastewater Collection Network
02

## Slide 9: Equations Used in SewerCAD
Hydraulic grade line:
HGL = Y + Z
Energy grade line:
EGL = Y + Z +
Manning's equations:
The most commonly used equation in open channel and sewage.
Where:
Y: Pressure head.
Z: Elevation.
: Velocity head.
Q: Flow (m3/s).
N: Manning Roughness Coefficient.
A: Flow area of the pipe, culvert or channel. (m²)
R: Hydraulic Radius =A/P. (m)
S: Downward (longitudinal) Slope of the conduit. (m/m)
P: Wetted perimeter which is the portion of the circumference that is contact with water. (m)

## Slide 10: wastewater load calculation
year | 1997 | 2007 | 2017 | 2021 | 2051
population | 1,239 | 1,735 | 2,092 | 2,239 | 6,137
Future population for Madama:
Domestic wastewater flow
= (Per capita water demand wastewater generation percentage peak factor future population ) + (infiltration percentage Per capita water demand wastewater generation percentage )
= (120 0.8 3 6,137) + (0.3 120 0.8) = 1,767 m3/d.

## Slide 11: Design Constrains
Cover depth (1-5 m).
Velocity (0.6-3 m/s).
Slope (1 % -12 %).
Conduit partially full system (75 %).
Minimum sewer diameters (not less than 8 inch).

## Slide 12: Manholes distribution and wastewater collection network layout
The load was equally distributed over all manholes.
Manholes were distributed every 30 meters and at intersections, taking into account the lack of conflict between the manholes and the obstacles on the ground.
Manholes and sewers are distributed to make the flow into the network by gravity.
Conduit
Manholes
Outfall

## Slide 13: Results
Diameters:
All diameter equal 8 in, as the color-coding in sewerCAD
Conduit
Manhole
Outfall

## Slide 14
Velocity:
all values is within the acceptable range (0.6 m/s - 3 m/s).
Chart: 

## Slide 15
Slope:
all values is within the acceptable range (1% - 12%).
Chart: 

## Slide 16
Cover (start) :
all values is within the acceptable range (1m – 5m).
Chart: 

## Slide 17
Cover (stop) :
all values is within the acceptable range (1m – 5m).
Chart: 

## Slide 18
Profiles :

## Slide 20: Cost of the Network
03

## Slide 21
Cost of the Network
Conduits cost
=50,336 $.
Manholes cost
=101,175 $.
Excavation Cost
=138,096 $.
Re - paving cost
=88,490 $
Backfilling cost
=77,463$.
Total cost of the Sewer collection network = 455,560 $
Cost per kilometer () = 133,988

## Slide 22: Recommendations
04

## Slide 23
Know we solve the problem of accumulate wastewater in cesspit. So, the next step is to think how we can treat this waste water and get the best utilization from it. therefor, we suggest a location in the end of the network to build a waste water treatment plant (WWTP).
This WWTP can achieve some environmental benefit:
Reduce the usage of potable water and replacing it with treated wastewater in manufacture or any other uses, to save water resources and expand agricultural areas, to produce various agricultural crops at lower financial value.
The WWTP could provide electricity in Advanced stages.
reducing the environmental pollution by disposing of the produced wastewater.
The produced sludge is a much cheaper and better replacement for the chemical fertilizers.

## Slide 24
The suggested location to built up is justify with
WWTP
contour map
political land map
LGU boundary map
Conduit
Manhole
Outfall
N
N
N

## Slide 25
agricultural areas map
nature reserves map
wells distribution map
N
N
N

## Slide 26
distance between house and WWTP
quarries distribution map
transportation network map
N
N
N