## Slide 1: Structural Analysis and Design of Al-Sayed Mall in Qalqilia
Prepared By:
Ahmad Mazen Abd-Alkareem Labat
Hamza Walid Shareef Dawoud
Mohammad Khaled Mohammad Nassoura
Mo'men Mahmoud Ahmad Khalifeh
Zaid Hilal “Mohammad-Rohi” Hijazi
Under supervision of:
Eng. Ibrahim Mohammad Arman

## Slide 2: Outline
Chapter One: Introduction
Chapter Two: Preliminary Design
Chapter Three: Three-dimensional analysis and design

## Slide 3: Chapter one: Introduction
Outline:
Project Plans and site location
Floors Information
Codes and standards
Software programs
Materials
Geotechnical investigations
Loads ( Gravity and lateral)
Load combinations

## Slide 4: Site location
Chapter One

## Slide 5: Site location
Chapter One

## Slide 6: Floors Information
Area for each floor is approximately equal to 1260 m2
Floor | Height (m) | Utilization
Basement two | 3.0 | Garages
Basement one | 3.8 | Stores
Ground floor | 5.0 | Stores
First floor | 3.8 | Stores
Second floor-forth floor | 3.8 | Offices
Fifth floor-Tenth floor | 3.8 | Hotels
Eleventh floor -twelfth floor | 3.8 | Lounge
Thirteenth floor | 3.8 | Restaurant
Chapter One

## Slide 7: Project plans
Chapter One

## Slide 8: Codes and standards
ACI 318-11 (American Concrete Institute)
IBC 2012 (International Building Code)
ASCE 7-10 (American Society of Civil Engineers)
ASTM 2016 (American Society for Testing and Materials)
AASHTO (American Association of State Highway and Transportation Officials)
Chapter One

## Slide 9: Software programs
ETABS 2016 (to analyze and design the model)
SAFE 2016 (to analyze and design the foundation)
AutoCAD 2018 ( to prepare the structural drawings)
Excel 2019 ( for calculation operations)
Chapter One

## Slide 10: Materials
Concrete
Structural Element | Concrete Type | fcʹ (MPa) | Ec (MPa) | ftʹ (MPa) | fr (MPa) | Poisson ratio | Ɣ (kN/m³)
Slabs, Beams and stairs | B400 | 32 | 2.66*104 | 1.87 | 3.51 | 0.2 | 25
Columns , Walls and foundation | B500 | 40 | 2.97*104 | 2.1 | 3.92 | 0.2 | 25
Chapter One

## Slide 11: Materials
Reinforcing steel
Yield strength (Fy) | 420 MPa
Ultimate strength (fu) | 620 MPa
Steel grade | 60
Modulus of elasticity (Es) | 200 GPa
Chapter One

## Slide 12: Materials
Nonstructural elements
Materials | Ɣ (kN/m³)
Mortar | 23
Tiles (porcelain) (3cm) | 27
Masonry stone (4cm) | 27
Bricks (20,15,10) | 15
Aggregates (filling materials) | 18
Plastering | 23
Glass clear float | 25
Aluminum | 26.1
Chapter One

## Slide 13: Soil investigations
Based on the available soil investigation report that has been taken from the NCTN Company in 22 January 2018, it was found that the soil is Medium Hard Rock (Sc) and the allowable bearing capacity is 3.6 kg/cm2
Chapter One

## Slide 14: Loads
Gravity loads
Dead load
Superimposed dead load
Slabs
Live load
Beams and external walls
Loads
Lateral loads
Soil load
Earthquake load
Temperature load
Chapter One

## Slide 15: Loads
Gravity load:
Dead load: Self weight of the structural elements.
Live loads: Referring to ASCE7-10 code
Live load was used as the table above, except the offices 5 kN/m2 has been used.
Type | Live load (kN/m2) | Type | Live load (kN/m2)
Heavy Stores | 12 | Offices | 2.5
Light Stores | 6 | Restaurant | 5
Generator room | 12 | Stairs and ramp | 5
Public rooms | 5 | Private rooms | 2
Chapter One

## Slide 16: Loads
Gravity load:
Superimposed loads on slab:
Floor layers (3.42 kN/m2)
Chapter One

## Slide 17: Loads
Gravity load:
Superimposed loads on slab:
False ceiling (0.25 kN/m2) if needed
Partitions
Area of the represented Zone m2
Type and length of partitions in the zone: Blocks (20cm) =17m, Blocks (10cm) =19.5m, Glass (1cm) =10.2m
Chapter One

## Slide 18: Loads
Gravity load:
Superimposed loads on slab:
Weight of block partitions (20cm)= 0.2×15+0.04×23.×3.8=14.9𝑘𝑁/𝑚
Weight of block partitions (10cm) = 0.1×15+0.04×23.×3.8=9.2𝑘𝑁/𝑚
Weight of glass partitions (1cm)
Chapter One

## Slide 19: Loads
Temperature load: Due to large length of the structure, temperature load has been used rather than using of expansion joint. And it is equal to 15 °C due to average change of the temperature during the day.
Chapter One

## Slide 20: Loads
Lateral loads:
from “Occupation” maps
Spectral response acceleration:
SS =0.28 S1 =0.08
Site coefficient:
FV =1.7 Fa =1.2
Spectral acceleration:
SMS =
Chapter One

## Slide 21: Loads
Lateral loads:
The design spectral acceleration parameters:
Chapter One

## Slide 22: Loads
Lateral loads:
Risk category (III) (ASCE 7-10)
Importance factor (Ie) = 1.25 (ASCE 7-10 )
Seismic design category (SDC)  C (ASCE 7-10)
Redundancy factor (ρ) = 1.0 (ASCE 7-10 )
Chapter One

## Slide 23: Loads
Lateral loads:
seismic forces resisting system:
The seismic forces resisting system was chosen to be “Building frame system-ordinary reinforced concrete shear wall”
Response modification coefficient (R) = 5
Overstrength factor (Ω0 ) = 2.5
Deflection amplification factor (Cd) = 4.5
Chapter One

## Slide 24: Loads
Lateral loads:
T0 = 0.2 * = 0.081 second
TS = = 0.405 second
TL = Long-period transition period (s)
it is equal to 10 seconds
Chapter One

## Slide 25: Loads
Lateral loads:
Soil load:
the building contains two underground floors (basement walls), thus they are subject to static rest earth pressure
+
, = 20 , = 6.8m
,
Chapter One

## Slide 26: Loads
Lateral loads:
Soil load:
So, 𝐻=𝑃0+Δ𝑃=57.94+7.32=65.26𝑘𝑁/𝑚2
Effect of Vehicles movement on basement walls:
AASHTO code recommended to add 12 kN/m2 as a uniform distributed load as surcharge on soil
So the total pressure effects on the basement walls at z=0 equal to 12.43 kN/m2 and at z=6.8 equal to 70.4 kN/m2( effect of the surcharge load =0.426×12=5.11 kN/m2).
Chapter One

## Slide 27: Load combinations
Factored load combinations:
1.4D + 1.6H
1.2D + 1.6L + 1.6H Where: 𝐸=𝐸ℎ+𝐸𝑣 𝐸=𝐸ℎ−𝐸𝑣
1.2D + 1.0E + L + 1.6H 𝐸ℎ=𝜌𝑄𝐸 𝐸𝑣=0.2𝑆𝐷𝑆𝐷
0.9D + 1.0E + 0.9H 𝑄𝐸𝑥=𝐸𝑄𝑥+0.3𝐸𝑄𝑦
D + L +T 𝑄𝐸𝑦=𝐸𝑄𝑦+0.3𝐸𝑄𝑥
Chapter One

## Slide 28: Load combinations
Service load combinations:
D + H
D + L + H
D + 0.7E + H
D+ 0.75L + 0.75(0.7E) + H
0.6D + 0.7E + 0.6H
Chapter One

## Slide 29: Chapter Two: Preliminary Design
Outline:
Slab structural system
Preliminary slab thickness
Preliminary dimensions of beams
Preliminary dimensions of columns
Preliminary dimensions of walls

## Slide 30: Slab structural system
Due to large spans length, two way slabs system was used.
Chapter Two
Slab of | Type of slab
Basement two floor -Third floor | Solid Slab
Forth floor - Thirteenth floor | Voided Slab

## Slide 31: Preliminary slab thickness
For solid slab
According to the average values of beam to slab flexural stiffness ratio () for the four sides of panel.
Try h= 300mm
Chapter Two

## Slide 32: Preliminary slab thickness
For solid slab
Assume steel cover = 40mm
=
So, preliminary thickness is OK
Chapter Two

## Slide 33: Preliminary slab thickness
For Voided slab
Try h = 40cm
The section dimensions is ok
Chapter Two

## Slide 34: Preliminary slab thickness
For Voided slab
Assume steel cover = 40mm
Ok
Chapter Two

## Slide 35: Preliminary dimensions of beams
Chapter Two
Beams location | Dimensions
In the external perimeter within shear walls. | 1000mm depth and 300mm width
In the elevators and stairs | 1000mm depth and 300mm width
In the roof slab | 500mm depth and 600mm width
In the Solid Slab | 500mm depth and 800mm width
In the Voided Slab Slab | 400mm depth and 800mm width

## Slide 36: Preliminary dimensions of beams
Layout of the beams:
Chapter Two

## Slide 37: Preliminary dimensions of columns
Tributary area between columns:
Chapter Two

## Slide 38: Preliminary dimensions of columns
Columns groups and dimensions based on tributary area:
Chapter Two
Floors | Column1 | Column2 | Column3 | Column4 | Column5
B2-F1 | 1000600mm | 13001300mm | 1400650mm | 1250600mm | 700300mm
F2-F5 | 700600mm | 11001100mm | 1200550mm | 900600mm | 700300mm
F6-F9 | 500600mm | 850850mm | 900450mm | 600600mm | 700300mm
F10-F13 | 300600mm | 600600mm | 700300mm | 300600mm | 700300mm
Floors | Column1 | Column2 | Column3 | Column4 | Column5
B2-F1 |  |  |  |  | 
F2-F5 |  |  |  |  | 
F6-F9 |  |  |  |  | 
F10-F13 |  |  |  |  | 

## Slide 39: Preliminary dimensions of walls
Assume the thickness of the shear walls equal to 30 cm
For the ground floor:
For the second basement floor:
Chapter Two

## Slide 40: Chapter Three: Three-dimensional analysis and design
Outline:
Structural modeling of the building.
Evaluation of the preliminary design.
Verification of the structural analysis.
Seismic forces checks.
Structural irregularity.
Effect of P-delta.
Deflection computations.
Design of beams
Design of columns
Design of slabs
Design of walls
Design of Footings
Design of stairs
Design of ramp

## Slide 41: Structural modeling of the building

## Slide 42: Structural modeling of the building
Section modifiers for flexure and torsion:
Slab modifiers = 0.25
Beams modifiers = 0.35
Wall modifiers = 0.7
Columns modifiers = 0.7
Ramp and stairs modifiers = 0.001
Some of the exterior and interior beams are failed due to shear or torsion stresses. So, modifier for some of these beams has been changed to reduce the torsion moment to . The dimensions of the other beams has been changed.
Chapter Three

## Slide 43: Structural modeling of the building
Chapter Three
Final sections modifiers

## Slide 44: Structural modeling of the building
Final sections modifiers
Chapter Three

## Slide 45: Structural modeling of the building
Load definition:
Chapter Three

## Slide 46: Structural modeling of the building
Load definition
Parameters of seismic forces in X and Y direction.
The values of SS, S1 and site class coefficient were changed in both directions until the values of SDS and SD1 reached the previously calculated values.
Chapter Three

## Slide 47: Structural modeling of the building
Masses
The total seismic load (w) includes: 100% from dead loads and superimposed dead loads, in addition to 25% from live loads
Chapter Three

## Slide 48: Structural modeling of the building
Functions
Response Spectrum function was defined in ETABS software based on ASCE 7-10 code.
Load cases
In response spectrum method, two load cases were defined, based on assumption that 100% of the force in one direction plus 30% of the force in the perpendicular direction and vice versa.
Chapter Three

## Slide 49: Evaluation of the preliminary design
Beams final dimensions:-
Type of slab | Final sections
Solid slabs | Beam 800500mm
 | Beam 1000500mm
 | Beam 300800mm
 | Beam 200500mm
Voided slabs | Beam 800400mm
 | Beam 1000400mm
 | Beam 300800mm
 | Beam 200500mm
Roof slab | Beam 600500mm
Type of slab | Final sections
Solid slabs | 
Voided slabs | 
Roof slab | 
Chapter Three

## Slide 50: Evaluation of the preliminary design
Final dimensions of columns:-
Chapter Three
Floors | Column1 | Column2 | Column3 | Column4 | Column5 | Column6
B2-F1 | 1000600 | 12501250 | 1400800 | 1250600 | 1400600 | 1600800
F2-F5 | 700600 | 11001100 | 1200600 | 900600 | 900500 | 1600800
F6-F9 | 500600 | 850850 | 1000500 | 600600 | 900500 | 1600800
F10-F13 | 300600 | 600600 | 900400 | 300600 | 900500 | 1600800
Floors | Column1 | Column2 | Column3 | Column4 | Column5 | Column6
B2-F1 |  |  |  |  |  | 
F2-F5 |  |  |  |  |  | 
F6-F9 |  |  |  |  |  | 
F10-F13 |  |  |  |  |  | 

## Slide 51: Verification of structural analysis
1- Compatibility of the structure
Chapter Three

## Slide 52: Verification of structural analysis
2- Equilibrium check:
Soil load from ETABS software:-
Chapter Three

## Slide 53: Verification of structural analysis
2- Equilibrium check:
Comparison between manual calculations and program results:
Manual calculation for soil load:
Chapter Three
Loads | Manual calculations | ETABS calculations | Difference percentage
Dead load (KN) | 255742.738 | 252719.2084 | 1.2%
Superimposed dead load (KN) | 135430.851 | 135426.3356 | 0%
Live load (KN) | 91407.97 | 91407.5226 | 0%

## Slide 54: Verification of structural analysis
3- Stress strain check:
The manual moment values of the slab and the beam were calculated on the internal span with 6m length inside the frame that shown below in basement two floor by using Direct Design Method.
Chapter Three
9m

## Slide 55: Verification of structural analysis
3- Stress strain check:
Slab: Mo from ETABS for an internal span in frame within the slab.
Mo from ETABS software
Mo manual
Difference percentage
Chapter Three

## Slide 56: Verification of structural analysis
3- Stress strain check:
Beam: ETABS results for Beam:-
Mo from ETABS software
Mo manual
Difference percentage
Chapter Three

## Slide 57: Verification of structural analysis
3- Stress strain check:
Column: ETABS results for a column:-
Axial force from ETABS software
Axial force from manual calculations
Difference percentage
Chapter Three

## Slide 58: Seismic forces checks
The Response Spectrum method was used mainly for seismic analysis and design, also the Equivalent Static method was used to make equilibrium check for base shear.
Base shear check:
VESx VRSx= 10743.74KN
VESy VRSy= 8614.3KN
New scale factor in x-direction
New scale factor in y-direction
Chapter Three
Direction | Manual (kN) | ETABS (kN) | Difference percentage
Vx | 22425.6 | 22218.97 | 1.0%
Vy | 10026.1 | 9950.73 | 0.96%

## Slide 59: Seismic forces checks
Story forces check: Vx = CVX* Base shear value
Chapter Three
Story | hi (m) | Wi (kN) | hik | Wi * hik | CVX | VX (kN) | VETABS (kN) | Difference percentage
F14 | 65 | 3574.77 | 83.50 | 298494.39 | 0.0189 | 419.41 | 298.56 | 40%
F13 | 61.2 | 22063.89 | 78.34 | 1728377.40 | 0.1093 | 2428.53 | 2307.25 | 5%
F12 | 57.4 | 22416.51 | 73.19 | 1640644.61 | 0.1038 | 2305.26 | 2343.28 | -2%
F11 | 53.6 | 22264.17 | 68.06 | 1515378.88 | 0.0958 | 2129.25 | 2165.49 | -2%
F10 | 49.8 | 22370.63 | 62.96 | 1408449.81 | 0.0891 | 1979.00 | 2013.67 | -2%
F9 | 46 | 24114.09 | 57.88 | 1395706.85 | 0.0883 | 1961.10 | 1968.55 | 0%
F8 | 42.2 | 23839.92 | 52.82 | 1259319.45 | 0.0796 | 1769.46 | 1799.20 | -2%
F7 | 38.4 | 23839.92 | 47.80 | 1139451.42 | 0.0721 | 1601.03 | 1627.92 | -2%
F6 | 34.6 | 23839.92 | 42.80 | 1020294.11 | 0.0645 | 1433.61 | 1457.66 | -2%
F5 | 30.8 | 24714.31 | 37.83 | 935001.32 | 0.0591 | 1313.76 | 1311.24 | 0%
F4 | 27 | 24685.68 | 32.90 | 812251.85 | 0.0514 | 1141.29 | 1159.73 | -2%
F3 | 23.2 | 27265.73 | 28.02 | 763896.38 | 0.0483 | 1073.34 | 1092.33 | -2%
F2 | 19.4 | 27539.91 | 23.18 | 638311.02 | 0.0404 | 896.89 | 911.87 | -2%
F1 | 15.6 | 28789.11 | 18.40 | 529590.72 | 0.0335 | 744.12 | 739.81 | 1%
G | 11.8 | 29931.70 | 13.68 | 409568.28 | 0.0259 | 575.48 | 559.96 | 3%
B1 | 6.8 | 29982.76 | 7.63 | 228734.15 | 0.0145 | 321.39 | 329.58 | -2%
B2 | 3 | 27993.67 | 3.20 | 89703.27 | 0.0057 | 126.04 | 132.87 | -5%
Total |  |  |  | 15813173.92 | 1.00 | 22218.97 |  | 

## Slide 60: Seismic forces checks
Period check:
, where 𝑇𝑎= 𝐶𝑡 ℎ𝑛𝑥=0.0488×(61.2)0.75=1.0678sec
sec
In general model, the fundamental period from ETABS software was equal to 1.385 seconds which less than the allowable upper limit 1.738 seconds.
Chapter Three

## Slide 61: Seismic forces checks
Modal mass participation ratios:
Both directions must be greater than or equal to 90% when using the Response Spectrum method and this thing was achieved when 25 modes were used in analyzing process in ETABS. where the sum of the modal mass participation ratios in x-direction was equal to 0.9053 and in y-direction was equal to 0.9593.
Chapter Three

## Slide 62: Structural irregularity
Horizontal irregularities
Type | Description | Comments
1a | Torsional Irregularity | Exist
1b | Extreme Torsional Irregularity | Exist
2 | Reentrant Corner Irregularity | Not needed to be checked, as the seismic design category is C
3 | Diaphragm Discontinuity Irregularity | Not needed to be checked, as the seismic design category is C
4 | Out-of-Plane Offset Irregularity | Not exist
5 | Nonparallel System Irregularity | Exist
Chapter Three

## Slide 63: Structural irregularity
Vertical irregularities:
Type | Description | Comments
1a | Stiffness-Soft Story Irregularity: | Not needed to be checked, as the seismic design category is C
1b | Stiffness-Extreme Soft Story Irregularity: | Not needed to be checked, as the seismic design category is C
2 | Weight (Mass) Irregularity: | Not needed to be checked, as the seismic design category is C
3 | Vertical Geometric Irregularity: | Not needed to be checked, as the seismic design category is C
4 | In-Plane Discontinuity in Vertical Lateral Force-Resisting Element Irregularity: | Not exist
5a | Discontinuity in Lateral Strength–Weak Story Irregularity: | Not exist
5b | Discontinuity in Lateral Strength–Extreme Weak Story Irregularity: | Not exist
Chapter Three

## Slide 64: Effect of p-delta
All values are less than
0.1, So, no need for
use the second order analysis.
Chapter Three

## Slide 65: Deflection computations
Immediate and long term deflections
= 2
Assume 50% sustained live loads and 50% un-sustained live loads, so
Load combination = 2 Dead loads + 2 Superimposed dead loads + 1.5 Live loads
Chapter Three

## Slide 66: Deflection computations
Drift check:
M equal to 16.63mm is less than allowable which equal to 57mm.
Chapter Three

## Slide 67: Design of beams
General
Beams should have at least two longitudinal bars continuous along both the top and bottom faces.
axial force due to temperature loads should be taken into consideration.
For tension axial force:-
At least minimum area of steel should be detailed as continuous bars along the top face and the other steel should be detailed as cutoff bars.
At least a quarter of required area of steel should be detailed as continuous bars along the bottom face and the other steel should be detailed as cutoff bars.
Chapter Three

## Slide 68: Design of beams
General
Beam details layout:-
Chapter Three

## Slide 69: Design of beams
General
For development length calculations:-
In some cases:-
For diameters < 20mm
For diameters ≥ than 20mm
In other cases:-
For diameters < 20mm
For diameters ≥ than 20mm
Chapter Three

## Slide 70: Design of beams
General
In top bars with tension steel and the thickness of the concrete below them are greater than 300mm, the development length must be multiplied by an amplification factor of 1.3.
8
Standard hock
Chapter Three

## Slide 71: Design of beams
General
Maximum spacing of stirrups for shear and torsion:-
Chapter Three
Required Vs | Maximum spacing (mm) |  |  |  |  | 
 | Non-prestressed beam |  |  |  |  | 
 | maximum spacing of legs of shear reinforcement across width of the member |  |  | Maximum spacing of legs of shear and torsion reinforcement along the length of the member |  | 
 | Lesser of | d | 600 | 300 | Ph/8 | d/2
 | Lesser of | d/2 | 300 |  |  | d/4
Required Vs | Maximum spacing (mm) |  |  |  |  | 
 | Non-prestressed beam |  |  |  |  | 
 | maximum spacing of legs of shear reinforcement across width of the member |  |  | Maximum spacing of legs of shear and torsion reinforcement along the length of the member |  | 
 | Lesser of | d | 600 | 300 | Ph/8 | d/2
 | Lesser of | d/2 | 300 |  |  | d/4

## Slide 72: Design of beams
General
The stirrups were condensed at a quarter of clear span length.
The longitudinal torsion bars must be distributed on the perimeter of the stirrups, where the distance between the adjacent bars does not exceed 300 mm.
Chapter Three

## Slide 73: Design of beams
Design check
Design check was done on beam B24-1 in third floor with width equal to 800mm, depth equal to 500mm.
Chapter Three

## Slide 74: Design of beams
Design check
For negative moment = 404.47kN.m
Shear force = 372.4kN
\
\
Chapter Three

## Slide 75: Design of beams
Design check
Torsion = 39.1kN.m
Axial Force = 9.56kN compression
Chapter Three

## Slide 76: Design of beams
Design
The design sample has been done on beam B24-1 in third floor with width equal to 800mm, depth equal to 500mm and cover equal to 60mm.
Design results of beam B24-1:-
Chapter Three

## Slide 77: Design of beams
Design
One-third of AL was added to the longitudinal reinforcing.
Torsion longitudinal reinforcing = (2Ø20), so:-
(8Ø25)
(7Ø22)
It is required to place two stirrups across the width of the beam.
Use 2Ø12/200mm
Chapter Three

## Slide 78: Design of beams
Design
Beam B24-1 details:-
Chapter Three

## Slide 79: Design of columns
General
Columns having clear height less than or equal to five times the dimension of column (C1) shall be designed for the minimum shear of:-
The shear associated with development of nominal moment strengths of the column at each restrained end of the unsupported length.
The maximum shear from the ultimate load combinations that include “”, with “” increased by the over-strength factor (Ωo).
Chapter Three

## Slide 80: Design of columns
General
This check was performed on column C36, with dimensions of 1400800mm, and clear height equal to 3m.
Moment axial interaction diagram for column C36 at zero degrees:-
Chapter Three
Chart: M3 (KN.m)
| 0 | 3371.1747 | 5527.7034999999996 | 7057.4052000000001 | 7989.0403999999999 | 8405.5586000000003 | 8001.4687999999996 | 7039.3797999999997 | 5555.6648999999998 | 3555.2449999999999 | 0
 | 34169.0355 | 34169.0355 | 32254.5253 | 27381.1009 | 22279.626 | 16696.5701 | 12666.6464 | 8584.7385 | 4545.457 | 536.9467 | -5039.2322

## Slide 81
General
Moment axial
interaction diagram
for column C36 at
zero degrees:-
Chapter Three
Load Case/Combo |  | 
1.2D+1.6L+1.6H | 5064.5094 | 5900
1.4D+1.6H | 4959.3315 | 5750
1.2672D+L+EQx+0.3EQy+1.6H Max | 3494.0486 | 5400
1.2672D+L-EQx-0.3EQy+1.6H Max | 5206.6594 | 5950
1.2672D+L+EQx-0.3EQy+1.6H Max | 76.9269 | 3500
1.2672D+L+0.3EQx+EQy+1.6H Max | 9302.5541 | 7300
1.2672D+L-0.3EQx-EQy+1.6H Max | -548.9317 | 3000
1.2672D+L-0.3EQx+EQy+1.6H Max | 10841.4738 | 7500
0.833D+EQx+0.3EQy+0.9H Max | 1453.9135 | 4000
0.833D-EQx-0.3EQy+0.9H Max | 3166.5243 | 5000
0.833D+EQx-0.3EQy+0.9H Max | -1963.2082 | 4100
0.833D+0.3EQx+EQy+0.9H Max | 7262.419 | 6500
0.833D-0.3EQx-EQy+0.9H Max | -2589.0667 | 2000
0.833D-0.3EQx+EQy+0.9H Max | 8801.3387 | 7000
1.2672D+Rx+L+1.6H Max | -1114.0171 | 2300
1.2672D+Ry+L+1.6H Max | 790.02 | 3200
0.833D+Rx+0.9H Max | -3154.1521 | 1700
0.833D+Ry+0.9H Max | -1250.1151 | 2500
D+L+T | 8350.7388 | 6950
D+L-T | 25.4696 | 3300
Load Case/Combo |  | 
1.2D+1.6L+1.6H | 5064.5094 | 5900
1.4D+1.6H | 4959.3315 | 5750
1.2672D+L+EQx+0.3EQy+1.6H Max | 3494.0486 | 5400
1.2672D+L-EQx-0.3EQy+1.6H Max | 5206.6594 | 5950
1.2672D+L+EQx-0.3EQy+1.6H Max | 76.9269 | 3500
1.2672D+L+0.3EQx+EQy+1.6H Max | 9302.5541 | 7300
1.2672D+L-0.3EQx-EQy+1.6H Max | -548.9317 | 3000
1.2672D+L-0.3EQx+EQy+1.6H Max | 10841.4738 | 7500
0.833D+EQx+0.3EQy+0.9H Max | 1453.9135 | 4000
0.833D-EQx-0.3EQy+0.9H Max | 3166.5243 | 5000
0.833D+EQx-0.3EQy+0.9H Max | -1963.2082 | 4100
0.833D+0.3EQx+EQy+0.9H Max | 7262.419 | 6500
0.833D-0.3EQx-EQy+0.9H Max | -2589.0667 | 2000
0.833D-0.3EQx+EQy+0.9H Max | 8801.3387 | 7000
1.2672D+Rx+L+1.6H Max | -1114.0171 | 2300
1.2672D+Ry+L+1.6H Max | 790.02 | 3200
0.833D+Rx+0.9H Max | -3154.1521 | 1700
0.833D+Ry+0.9H Max | -1250.1151 | 2500
D+L+T | 8350.7388 | 6950
D+L-T | 25.4696 | 3300

## Slide 82: Design of columns
General
The maximum shear (V2) obtained from the ultimate load combinations after increasing earthquake load (E) by over-strength factor (Ωo) equal to 2018KN.
2018kN < 5000kN, so column C36 shall be designed for 2018kN.
\
Chapter Three

## Slide 83: Design of columns
Design check
Design check was performed on column C11 with dimensions of 12501250mm.
Design information of column C11:-
The reciprocal load method was used.
Chapter Three

## Slide 84: Design of columns
Design check
ρ=1.29%
Moment axial interaction diagram for column C11 at zero degrees:-
Chapter Three
Chart: M3 (KN.m)
| 0 | 4500.2058999999999 | 7270.2776000000003 | 9280.8575000000001 | 10587.861699999999 | 11329.099099999999 | 10793.952499999999 | 9612.2970999999998 | 7763.6093000000001 | 5227.4422000000004 | 0
 | 48712.0691 | 48712.0691 | 45648.8899 | 38662.5343 | 31234.9808 | 23060.0126 | 17522.6312 | 11958.3705 | 6331.883 | 732.7503 | -8449.0577

## Slide 85: Design of columns
Design check
Moment axial interaction diagram for column C11 at nineteen degrees:-
Using the moment axial interaction diagrams, and at the design moment values of both zero and nineteen degree curves, the nominal axial load strength along the zero degrees curve () equals 48700, also along the nineteen degrees curve () equals 48700.
Chapter Three
Chart: M2 (KN.m)
| 0 | 4500.2058999999999 | 7270.2776000000003 | 9280.8575000000001 | 10587.861699999999 | 11329.099099999999 | 10793.952499999999 | 9612.2970999999998 | 7763.6093000000001 | 5227.4422000000004 | 0
 | 48712.0691 | 48712.0691 | 45648.8899 | 38662.5343 | 31234.9808 | 23060.0126 | 17522.6312 | 11958.3705 | 6331.883 | 732.7503 | -8449.0577

## Slide 86: Design of columns
Design check
= 31598
Chapter Three

## Slide 87: Design of columns
Design
The design sample was performed on column C2 , with dimensions of 1400x800mm, and cover equal to 50mm.
Using diameter of bars equal to 20mm:-
, use 4020.
Chapter Three

## Slide 88: Design of columns
Design
Shear reinforcing required for column C2:-
Six stirrups in whole section were used.
Chapter Three

## Slide 89: Design of columns
Design
Use spacing between the stirrups equal to 300mm.
Column C2 details:-
Chapter Three

## Slide 90: Design of slabs
Mesh reinforcement with additional steel in some areas due to the increased load in them has been placed in both directions (X and Y).
The design check was made on a point with coordinates X= 24.6m, Y= 5.6m, in the third floor with 300mm thickness solid slab.
Using ETABS software, the positive moment value was taken from load combination 1.2D+1.6L+1.6H, which equal to 53kN.m.
Chapter Three

## Slide 91: Design of slabs
Using ETABS software, the bottom rebar area value at the same joint equal to 576 , so the design is correct.
Chapter Three

## Slide 92: Design of walls
General
Walls that have thickness exceeds 250mm shall have reinforcement for each direction placed in two layers parallel with faces of these walls.
The horizontal reinforcement was spliced at supports with development length of or larger, while the vertical reinforcement was spliced at the connection area between the two successive walls with development length of or larger.
Chapter Three

## Slide 93: Design of walls
Design check
Design check was performed on wall W-05 that exist in the second basement (B2) floor with thickness of 300mm and length equal to 20300mm.
Design information of wall W-05:-
Chapter Three

## Slide 94: Design of walls
Design check
This wall was modeled as a column in SAP2000 software.
After running and design the model, the column bending axial interaction ratio (P-M-M) was 0.885 , which is smaller than 1, so the design of ETABS software for this wall is correct.
Chapter Three

## Slide 95: Design of walls
Design
Set of piers and spandrels were defined in ETABS software.
Piers and spandrels in all walls were reinforced with the required steel reinforcement for each of them.
The design sample has performed on wall W-03 in the second basement (B2) floor with thickness of 400mm and length equal to 5871mm.
Chapter Three

## Slide 96: Design of walls
Design
Longitudinal reinforcing for wall W-03 from ETABS software:-
Longitudinal reinforcing per meter length
Longitudinal reinforcing in each layer
Use 118/200mm
Chapter Three

## Slide 97: Design of walls
Design
Shear reinforcing for wall W-03 from ETABS software:-
Shear reinforcing per meter length
Shear reinforcing in each layer
Use 116/90mm
Chapter Three

## Slide 98: Design of walls
Design
Wall W-03 details:-
Chapter Three

## Slide 99: Design of Footings
General
Mat foundation was used in this structure, and SAFE software was used to design this foundation.
The bearing capacity of the soil equal to 360, this value was increased due to the existing soil around the structure, as shown:-
Chapter Three

## Slide 100: Design of Footings
General
The thickness of the mat foundation was assumed to be 2.0m, and punching shear check was performed on this thickness:-
In the columns, the maximum axial force equal to 31578 KN, which is in column C11 with dimensions of 12501250mm.
Chapter Three

## Slide 101: Design of Footings
Mat foundation modeling
Concrete B500 (40MPa) was used for this mat foundation. It was defined in SAFE software with bending modifiers equal to 0.7.
An expand with a value of 2000mm was created at all sides of the mat foundation.
The design code selected in SAFE software is ACI 318-11 code.
Chapter Three

## Slide 102: Design of Footings
Evaluation of design
After running the model, the soil pressure under the mat from service combinations exceeded the bearing capacity of 480 KN/m2.
Therefore, piles with a diameter of 1 meter and a length of 20 meters were placed under the mat foundation every 3 meters, it was represented in SAFE software as a point spring.
The capacity of the pile was calculated by referring to “Principles of Foundation Engineering 8th edition”.
Chapter Three

## Slide 103: Design of Footings
Evaluation of design
using alpha method
Take factor of safety equal to 3.
It was assumed that the settlement in the piles is 14.5mm.
Point spring translation for the pile =
This point spring property were defined in SAFE software for all the piles.
Chapter Three

## Slide 104: Design of Footings
Evaluation of design
The layout of the piles under the mat foundation:-
Chapter Three

## Slide 105: Design of Footings
Evaluation of design
After running the model, the soil pressure in the mat and pile capacity didn’t exceed the bearing capacity of 480 KN/m2 and 2200KN, respectively.
Chapter Three

## Slide 106: Design of Footings
Shear check
The maximum shear force (Vu) in mat foundation was 1487kN.
Chapter Three

## Slide 107: Design of Footings
Reinforcement check
The moment value using safe software from load combination 1.2D+1.6L+1.6H at a point with coordinates of X= 24.2m, Y= 6.2 m, equal to 1427kN.m/m.
Chapter Three

## Slide 108: Design of Footings
Reinforcement check
Using SAFE software, the top rebar area value at the same joint equal to 3546, so the design is correct.
1Ø25/250mm top steel and 1Ø22/250mm bottom steel were used in mat foundation reinforcement using SAFE software.
Chapter Three

## Slide 109: Design of Footings
Punching shear check
In order for the design to be correct the punching shear ratio must be less than one.
Maximum value of punching shear ratio in mat foundation:-
Chapter Three

## Slide 110: Design of Footings
Piles reinforcement
Number of bars =
, so use 1818
Use spiral stirrups of 1Ø12/150mm.
Chapter Three

## Slide 111: Design of Stairs
General
This structure contains three stairs. Therefore, three models were created and represented in ETABS software.
For each stair:-
Height of the riser is 170mm.
Width of the tread (or going) is 300mm.
The thickness of landing is 200mm.
Concrete cover is 40mm.
Superimposed dead load equal to 5 KN/m2.
Live load equal to 5 KN/m2.
Chapter Three

## Slide 112: Design of Stairs
General
As example, the plan of stairs 3 was taken from the Architectural plans, and the three-dimensional (3D) view of for this stair was taken from ETABS software:-
Chapter Three

## Slide 113: Design of Stairs
Stairs shear check
Solid slab with thickness equal to 200mm and reinforcement cover of 40 mm has been used to all stairs.
kN
The maximum shear (Vu) was discovered in stairs 2 with value equal to 72.79 KN.
No need for shear reinforcement.
Chapter Three

## Slide 114: Design of Stairs
Stairs flexural reinforcement
The minimum flexural strength at section () has been calculated:-
= = 23.7
All moment values in ETABS software were less than minimum flexural strength at section ().
Chapter Three

## Slide 115: Design of Stairs
Stairs flexural reinforcement
So, all steel reinforcement will be shrinkage steel in both directions (1∅12/250mm).
Moment values in stairs (M11) using ETABS software:-
Chapter Three

## Slide 116: Design of Stairs
The typical detailed reinforcement for all stairs:-
Chapter Three

## Slide 117: Design of Ramp
Ramp flexural reinforcement
The ramp was analyzed manually with 250mm thickness as one way solid slab in one direction and use minimum reinforcement steel in the other direction.
For the ramp:-
Live Load = 5kN/m2
Superimposed dead load = 1.15kN/m2
Own weight = = 6.25kN/m2
= = 0.00636
Chapter Three

## Slide 118: Design of Ramp
Ramp flexural reinforcement
0.00636 1000 210 1336
= 0.00182501000 = 450
Use 120/200mm, for the other direction use 112/250mm
Detailed reinforcement for the ramp:-
Chapter Three

## Slide 119
The End