## Slide 1: Qabatia Storm Water Sewer System
- Jamal Nazzal
- Diaa Tamimi
- Ahmad Amarni

## Slide 2: Project Objectives
understand the problem of Qabatia rainfall-runoff process. And
Improve the current stormwater routing structures. By
Using StormCAD software to design and expand the current network.

## Slide 3: General description of Qabatia
Located 9 kilometers south-west of Jenin.
300 meters above sea level.
Its area is 6000 donums.
A valley surrounded by mountains.
Around 30000 capita occupy the area of Qabatia.

## Slide 4: Catchment Area
A catchment can be defined as the total area of land that drains to a particular point along a stream.
Water flows perpendicular to contour lines in the direction of the slope.
Flow paths, and divides were drawn.
Main flow paths were determined.
Civil 3D was used.

## Slide 8: Stream topology and order
Stream topology and order helps the designer understand and predict the locations and dimensions of various hydraulic structures.

## Slide 11: The IDF Curves
Using the measurements from short duration rainfall, a series of rainfall curves (IDF curves) are prepared for practical use in engineering work.
Different stations are Located, and are given weight with respect to that area.

## Slide 12: the IDF data for Nablus city, used for Qabatia

## Slide 13
Chart: Annual Rainfall Hyetograph
1996 | 599
1997 | 488
1998 | 421
1999 | 514
2000 | 420
2001 | 529
2002 | 551
2003 | 566
2004 | 531
2005 | 415
2006 | 629
2007 | 411

## Slide 14: Theory And Methods of Computation
Manning’s Equation
Darcy-Weisbach Equation
Hazen-Williams Equations
The Rational Method
  Morgali and Linsley Method
  Kirpich Method
  Kerby-Hatheway Method
  The Federal Aviation Administration equation
Shreve

## Slide 15: THE RATIONAL METHOD
Proposed in 1889,a formula for the estimation of peak flow rate from small catchment areas
Q = design discharge
C = runoff coefficient
I = design rainfall intensity
A = watershed drainage area

## Slide 16: Basic assumptions of the rational method
The max. runoff rate at any location is a function of the average rainfall rate during the time of concentration for that location.
The max. rainfall rate occurs during the time of concentration.

## Slide 17: Runoff Coefficient C
Type of surface | C
Concrete, asphalt, solid rock | 0,8-0,9
Gravel | 0,4-0,6
Farmland, parks | 0,2-0,4
Woodland | 0,1-0,2
R = Total depth of runoff
P = Total depth of precipitation

## Slide 18: Time of Concentration tc
The flow time from the most remote point in the drainage area to the point in question.
Usually is equal to an overland flow time plus a channel flow time.
channel flow time estimation = channel length / avg. full-flow velocity

## Slide 19: Methods for computing the overland tc
Morgali and Linsley Method
Kirpich Method
Kerby-Hatheway Method
The Federal Aviation Administration equation

## Slide 20: Morgali and Linsley Method 1965
For small urban areas < twenty acres
Planar drainage
  tc = time of concentration (min)
  i = design rainfall intensity (in/hr)
  n = Manning surface roughness (dimensionless)
  L = length of flow (ft)
  S = slope of flow (dimensionless)

## Slide 21: Notes on Morgali’s
The Morgali and Linsley equation is implicit in that it cannot be solved for tc without i. So, iteration is required.
Solution can be achieved by combining Morgali’s with the intensity equation
Then solving using a numerical method (such as a calculator solver). The solution of the two equations yields both tc and i.

## Slide 22: Kirpich Method 1940
For small drainage basins that are dominated by channel flow
tc = time of concentration (min),
L = length of main channel (ft), and
S = main channel slope (ft\ft).
Computed tc is multiplied by 0.4 for overland flow path that are concrete or asphalt, and by 0.2 where the channel is concrete lined.
Limited to watershed with a drainage area of about 200 acres

## Slide 23: Kerby-Hatheway Method 1959
For small watersheds for computing the overland flow.
tc = time of concentration (min),
N = Kerby roughness parameter (dimensionless), and
S = overland flow slope (dimensionless).

## Slide 24: A combination
Overland flow rarely occurs for distances exceeding 1200 feet.
So, if the watershed length exceeds 1200 feet, then a combination of Kerby’s equation (Overland Flow) and the Kirpich equation (channel tc) may be appropriate.
Values for Kerby’s roughness parameter N are presented on the following table

## Slide 25: The Federal Aviation Administration equations 1965
A simple estimation of tc that is widely used in combination with the Rational Method (CIA)
C= the rational coefficient
L= overland flow length
S= surface slope in %

## Slide 26: Time of Concentration tc
It is recommended that tc be less than 300 minutes and greater than 10 minutes
  The concept is that estimates of i become unacceptably large for durations less than 5 or 10 minutes
  For long durations (such as longer than 300 minutes), the assumption of a relatively steady rainfall rate is less valid.

## Slide 27: Stream Order

## Slide 28: Open Channel flow and energy losses equations
Manning’s equation
Darcy-Weisbach equation
Hazen-Williams equation

## Slide 29: Manning’s equation
Gravity full flow occurs at that condition where the conduit is flowing full, but not yet under any pressure
Analysis of open-channel flow in a closed conduit is no different than any other type of open-channel flow.
In gravity flow conditions, manning's discharge formula is applicable for the discharge of pipes and culverts.
Q is Discharge
n is Manning’s coefficient
A is the cross-sectional area
R is the hydraulic radius
S is the slope of the pipe

## Slide 30
Due to the additional wetted perimeter and increased friction that occurs in a gravity full pipe, a partially full pipe carries greater flow.
For a circular conduit the peak flow occurs at 93 percent of the height of the pipe, and the average velocity flowing one-half full is the same as gravity full flow.

## Slide 31: Darcy-weisbach equation
RN>2000
Based on the Colebrook equation.
=
Moody diagram can also be used

## Slide 32: Moody diagram

## Slide 33: Hazen-Williams equation
V=CHR0.63S0.54
CH= the hazen-willliams coefficient

## Slide 35
Pre-Design

## Slide 36: Assumptions
1- Gravity flow (manning’s eqn):
Part full.
Flow from higher to lower elevation.

## Slide 37: Assumptions
2- Rational Method for surface discharge:
Q=CiA
Rainfall is uniform along the entire catchment area.
Rainfall intensity is constant.
    The discharge rate assumes that every point in the catchment contributes to the outfall.

## Slide 38: Assumptions
3- Time of concentration:
Method used: FAA equation
Convert tc from hrs to mins

## Slide 39: Assumptions
4- Surface flow:
All streets are surrounded by high-curb sidewalks
Water doesn’t cross from streets to land or vice-versa
All surface discharge enters the catch basin at the lowest point

## Slide 40: Definition of network elements
1- Pipes:
Concrete (n=0.013)
Circular
Minimum diameter = 16” (400mm)

## Slide 41: Definition of network elements
2- Catch basins:
Location: in sag
Desired sump depth = 2m
Clogging factor = 20%
Shape: sqaure
Structural width = 0.9m
Grate width = 0.8m

## Slide 42: Definition of network elements
3- Manholes:
Diameter = 36”
Serves as a point of intersection of two or more pipes
Where there’s change in alignment or slope

## Slide 43: Definition of network elements
4- Catchment areas:
Drawn using the positions of catch basins
C values were determined for each catchment
Tc values were determined using FAA method
For urban areas increase Tc<5 to 5

## Slide 44: Definition of network elements
5- IDF Data
The data used was for a return period= 5 years

## Slide 45: Definition of network elements
6- street-crossing culverts
Shape: box
Material : concrete (n=0.013)
Depth = 30 cm
Width range: [30cm-180cm]

## Slide 46: Network layout considerations
Loops are prohibited; only 1 downstream pipe
On street paths, directed to open channel
Catch basins are appointed where there’s water accumulation

## Slide 47: Network layout considerations
Street-crossing culverts are assigned to allow flow streams to cross the street section and reach the nearest catch basin
Or wherever its uneconomical to appoint a catch basin and connect it to the network

## Slide 48: Design constraints
Velocity:
Pipes: [0.6 – 6] m/s
Culverts: [0.6 – 8] m/s
Slope = [1 – 10] %
While 0.5% is allowable
Cover: [0.8 – 5] m
Water depth:
Pipes: 75%
Street culverts: 50%

## Slide 49
Post-Design

## Slide 50: Resulted errors
1- Cover exceeded:
Change pipe paths
2- Velocity exceeded:
Use drop manholes

## Slide 51: Resulted errors
Drop manholes profile

## Slide 52: Resulted errors
3- Main open channel (impractical depth)

## Slide 53: Resulted errors
Profile for that section

## Slide 54: Resulted errors
Alternative path; box conduit in land

## Slide 55: Results
Layout

## Slide 56: Results
Excavation = (GL – Invert elevation according to profiles) – Existing channel depth

## Slide 57: Results
1- Conduits:
Diameter range: [400mm-2250mm]
Velocity:

## Slide 58: Results
Cover:
Slope

## Slide 59: Results
2- Street-crossing culverts
Thickness = 30 cm
Span range: [30 – 180] cm
Velocity

## Slide 60: Results
Slope
High slopes are acceptable since velocities are within range, and there aren’t any links that could be damaged

## Slide 61: Results
3- Catchments surface discharge

## Slide 62: Results
4- Outfall discharge
Q= 44.49 m3/s
Less than sum of catchments discharge because of the accumulation of Tc with pipe lengths

## Slide 63: Recommendations
Covering the open channel but leaving openings for maintenance and to preserve open flow conditions.
Opening manhole covers in case of a storm event of a return period>5 to allow streams to reach the next catch basin.

## Slide 64: Recommendations
Use of bars at the opening of a street culvert in addition to a depression at the opening to retain large solids.
Use of reinforced concrete around street culverts’ parameters.
Use of anchors or rings around steep-slope culverts

## Slide 70: Thank You