## Slide 1: Integrated Redesign of a Fire Station in Nablus City
Prepared by:
Raghad Abu Hatab
Israa Sholi
Jawaher Sweedan
Supervisor:
Dr. Muhannad Haj Hussein

## Slide 2: TABLE OF CONTENTS Architectural Design 01 02 05 06 Structural Design Electro_Mechanical Design Fire & Safety Design Bill of Quantity
03
04
Site & Location
Environmental Design
Thermal Design
07
08

## Slide 3: Site & Location 01

## Slide 4
The fire station building is located in northern mountain of Nablus city, which lies in the north of west bank, approximately 30 mile north of Jerusalem. Nablus is about 550 m above sea level, on latitude 32.2 N and longitude 35.2 E.
The nuns building and other buildings surround the site on the north. On the south by AL Shuhada’ Street and the eastern Cemetery. While the east by Ibn Rushd Street and other buildings, finally on the west by the city police station and AL Haji Nimr Nabulsi Mosque.
Fire Station
Mosque
Police Station

## Slide 5: FIRST CONCEPT Architectural Design
Neptune is the fourth-largest planet by diameter in the entire Solar System
02

## Slide 6: The site-before

## Slide 7: The site-after

## Slide 8
Ground floor-before

## Slide 9
Ground floor–after

## Slide 10
First floor–after

## Slide 11
Second floor–after

## Slide 12
Elevations
North elevation
South elevation
South elevation

## Slide 13
Elevations
East elevation
West elevation

## Slide 14
Sections
Section A-A
Section B-B

## Slide 15: Thermal Design
03

## Slide 16: Material construction properties
Material | Thickness | K value (W/m.k)
Porcelain tile | 2 cm | 1.3
Cement mortar | 2 cm | 0.72
Sand | 7 cm | 2
Reinforced concrete | 10 cm | 1.9
EPS Expanded Polystyrene | 6 cm | 0.035
Ground Floor
U-value for ground floor = 0.487 W/m2.k.

## Slide 17: Material construction properties
Internal Floor
U-value for internal floor = 1.132 W/m2.k.
Material | Thickness | K value (W/m.k)
Porcelain tile | 2 cm | 1.3
Cement mortar | 2 cm | 0.72
Sand | 7 cm | 2
Reinforced concrete | 35 cm | 1.9
Air gap | 60 cm | −
Gypsum board | 1.2 cm | 0.16

## Slide 18: Material construction properties
External Wall
U-value for external wall = 0.343 W/m2.k.
Material | Thickness | K value (W/m.k)
Plaster | 1.3 cm | 0.8
Concrete block | 10 cm | 0.62
XPS Extruded Polystyrene - CO2 Blowing | 7.4 cm | 0.034
Concrete block | 10 cm | 0.62
Air gap with steel stud | 5 cm | −
Gypsum board | 1.2 cm | 0.16

## Slide 19: Material construction properties
Internal Wall
U-value for internal wall = 2.122 W/m2.k.
Material | Thickness | K value (W/m.k)
Plaster | 2 cm | 0.8
Concrete block | 10 cm | 0.62
Plaster | 2 cm | 0.8

## Slide 20
Element | Finish material | ɑ at 125 Hz | ɑ at 250 Hz | ɑ at 500 Hz | ɑ at 1000 Hz | ɑ at 2000 Hz | ɑ at 4000 Hz
Wall | Plaster | 0.03 | 0.03 | 0.04 | 0.05 | 0.04 | 0.03
Ceiling | Suspended ceiling | 0.26 | 0.57 | 0.63 | 0.96 | 0.44 | 0.56
Floor | Porcelain tile | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02
Floor | Wood | 0.1 | 0.36 | 0.99 | 0.99 | 0.5 | 0.35
Door | Solid Wood | 0.15 | 0.11 | 0.1 | 0.07 | 0.06 | 0.07
Chair | Leather | 0.44 | 0.54 | 0.6 | 0.62 | 0.58 | 0.5
Chair | fabric | 0.19 | 0.37 | 0.56 | 0.67 | 0.61 | 0.59
Chair | wood | 0.15 | 0.19 | 0.22 | 0.39 | 0.38 | 0.3
Window | Double glass | 0.35 | 0.25 | 0.18 | 0.12 | 0.07 | 0.09
 | Baffle | 0.23 | 0.6 | 0.99 | 0.99 | 0.99 | 0.99
The absorption coefficient for the finished material:
Acoustical Design
The standard value for RT60:
Zone | Reverberation time (RT60)
Office | 0.4-1.0 Sec
Theater | 0.6-1.3 Sec
Dining Room | <1.4 Sec
Bedroom | 0.4-1.1 Sec
Quit Study Room | 0.4-0.6 Sec
Gymnasium | 1.0-1.5 Sec

## Slide 21: Acoustical Design
The reverberation time for the office according to Sabine:

## Slide 22: Acoustical Design
The reverberation time for the theater according to Sabine:

## Slide 23: Acoustical Design
The reverberation time for the dining room according to Sabine:

## Slide 24: Acoustical Design
The reverberation time for the bedroom according to Sabine:

## Slide 25: Acoustical Design
The reverberation time for the study room according to Sabine:

## Slide 26: Acoustical Design
The sound transmission loss for the internal walls between different spaces:
Room Being Considered | Adjacent Area | STC Level (dB)
Bedroom | Corridor | 45
 | Study Room | 45
 | Bedroom | 52
Conference Room | Corridor | 42
 | First Aid Room | 45
Store | Corridor | 40
 | Gymnasium | 53
First Aid Room | Corridor | 40
Dining Room | Corridor | 50
 | Bedroom | 50
 | Kitchen | 50
Gymnasium | Corridor | 53
Study Room | Corridor | 53
Sound Transmission Loss (STC)

## Slide 27: Acoustical Design
The Impact insulation class for the internal floor = 56 dB and the calculated IIC for the floor should be more than 50 dB, so it’s ok.
Impact Insulation Class (IIC)

## Slide 28: Heating & Cooling load
The comfort graph for the station from Design Builder:

## Slide 29: Heating & Cooling load
Temperature and heat loss from Design Builder:
Temperature and heat gain from Design Builder:

## Slide 30: Heating & Cooling load
The site and source energy for the station from Design Builder:
The total site energy in the station is less than the baseline of the energy intensity equal to 278.1 kWh/m2, which is required.

## Slide 31: Enviromental Design
04

## Slide 32: Daylighting
Main modification for daylighting:
1. Used CNC.
2. Adding Cantilevers.
3. Adding Louvers.
4. Using low transmission glass.

## Slide 33
Daylight analysis for the model for the ground floor before and after modification:
Before
After
Average daylight factor = (2-6)%

## Slide 34
Daylight analysis for the model for the first and second floors after modification:
Average daylight factor = (2-6)%

## Slide 35: Structural Design
05

## Slide 36
Our project is designed to carry live, dead and super imposed loads. The building has a seismic joint, so we have two parts as shown in the following figures:
Block one
Block one

## Slide 37
External buildings
The Tower
External rooms

## Slide 38
The Loads
Occupancy or use | Uniform live load (psf) | Uniform live load (KN /m2)
Gymnasium | 100 | 5
Other areas | 63 | 3
Live load from:
The_jordanian_national_building_code.
ICC IBC 2003
Super imposed dead = 4.5 KN / m2

## Slide 39
Definition of response spectrum seismic load
The building was analyzed and designed to resist seismic forces based on UBC 97 code.
The city, which will be held in building, is the city of Nablus.
Soil type is SE.
Seismic zone of Nablus is 2B (Z=0.20) as shown in seismic hazard map.
Importance factor: I = 1.25, as the building is classified as an essential building
Acceleration-dependent seismic Coefficient (Ca) =0.20
Velocity-dependent seismic Coefficient (Cv) =0.20
Force reduction factor, R= 5.5

## Slide 40
There are some checks through which we check if the outputs and results of the ETABS program are correct. These checks have been done as the following:
Compatibility check
Equilibrium check
Internal force check
Deflection check
Period check
Base shear check
Drift check
The checks

## Slide 41
Reinforcement design
Slab design

## Slide 42
Reinforcement design
Details of column 11
Column design

## Slide 43
Beam design

## Slide 44
Beam design
Cross-Section of B8
Longitudinal
Section in B8

## Slide 45
Shear wall design
Details of Shear wall 6
Shear wall 6

## Slide 46
Footing design
F15
Mat 0.9

## Slide 47
Footing design
Details of F15

## Slide 48
Water tank design
3D view of water tank
from SAP2000
Reinforcement details of water tank

## Slide 49
Water tank design
Section A-A of water tank
Section B-B of water tank

## Slide 50
Retaining walls design
Our project contains two different retaining walls in terms of loads, whereby the first wall is only exposed to soil load on one side, and the second wall is exposed to both soil load and live load on the road, so we will design them through the PROKON program.

## Slide 51
Retaining walls design
Cantilever wall (1)
Wall design and dimensions by PROKON.

## Slide 52
Retaining walls design
Section A in Cantilever wall (1)

## Slide 53
Retaining walls design
Section A in Cantilever wall (1)

## Slide 54
Steel structure design
Section | Group
HE240A | Top Cord
HE240A | Bottom Cord
HE240A | Bracing
HE240A | Column
Steel section of Umbrellas
3D view of Umbrellas from SAP2000

## Slide 55
Section | Group
L (40*40*3) | Top Cord
L (40*40*3) | Bottom Cord
CHS 88.9 * 3.2 | Bracing
CHS 323.9 * 6 | Column
Steel structure design
Steel section of theater
3D view of theater from SAP2000

## Slide 56: Electro-Mechanical Design
06

## Slide 57: Artificial lighting
The selected Luminaires inside the building:
SM400C
SM134V
Compass
DN130B
Venus
PT570P
Lucequadro
TPS760
SM150C
1/18W NS
Article name | Manufacturer | Luminous | Load
 |  | Lm | Watt
SM400C POE | PHILIPS | 4197 | 39
SM134V | PHILIPS | 2699 | 30.5
COMPASS | FLOS | 708 | 50
DN130B | PHILIPS | 2278 | 22
VENUS | LEDS C4 | 413 | 11
TPS760 | PHILIPS | 4431 | 108
SM150C | PHILIPS | 4799 | 45
1/18W NS HPF | NARDEEN | 810 | 18
TPS760 | PHILIPS | 4431 | 108
PT570P | PHILIPS | 2699 | 25
Lucequadro LED | 3F FILIPPI | 1904 | 28.2

## Slide 58: The selected Luminaires outside the building:
Article name | Manufacturer | Luminous | Load
 |  | Lm | Watt
MVP506 | PHILIPS | 21057 | 227
kamino130 led | ARES | 144 | 5.8
SPARKS 12 | SIMES | 159 | 44
SGS101 | PHILIPS | 3060 | 61
KTY234 | WEEF | 409 | 21
Flex Strip | PROLED | 120 | 1.4
COMPASS BOX | FLOS | 425 | 50
MaxiTube-Wall | UNILAMP | 895 | 84
MV P506
kamino
Spark S12
SGS101
KTY234
Flex Strip
Compass box
Maxi Tube

## Slide 59: Illuminance results from DIALux.evo for the general offices

## Slide 60: Illuminance results from DIALux.evo for the ground floor
Space | Lux | Required Lux | Uniformity | Required Uniformity | UGR | Required UGR
General Offices | 541 | 500 | 0.62 | 0.6 | 15.9 | 19
Watch Office | 636 | 500 | 0.54 | 0.6 | 15.1 | 19
Parking | 204 | 150 | 0.10 | 0.4 | - | 28
Reception Corridor | 223 | 200 | 0.42 | 0.4 | 19.8 | 22
Sanitary | 289 | 200 | 0.53 | 0.4 | - | 25
WC | 249 | 200 | 0.80 | 0.4 | - | 25
Stairs | 155 | 150 | 0.01 | 0.4 | - | 25

## Slide 61: Illuminance result from DIALux.evo for the first floor
Space | Lux | Required Lux | Uniformity | Required Uniformity | UGR | Required UGR
Bed Room | 380 | 300 | 0.53 | 0.6 | - | 19
Dinning Room | 61.6 | 50 | 0.16 | 0.01 | 15.2 | 22
Kitchen | 568 | 500 | 0.58 | 0.6 | 16.3 | 22
Theater Workplane | 503 | 500 | 0.004 | 0.6 | 17.2 | 19
Theater Inclined surface | 734 | 500 | 0.73 | 0.6 | - | 19
Theater Top | 582 | 500 | 0.73 | 0.6 | - | 19
Theater between | 788 | 500 | 0.86 | 0.6 | - | 19
Theater Bottom | 784 | 500 | 0.85 | 0.6 | - | 19
First Aid | 662 | 500 | 0.63 | 0.6 | 15.2 | 16

## Slide 62: Illuminance results from DIALux.evo for the second floor
Space | Lux | Required Lux | Uniformity | Required Uniformity | UGR | Required UGR
Gym | 401 | 300 | 0.065 | 0.6 | 11.4 | 22
Store | 149 | 100 | 0.4 | 0.4 | - | 25

## Slide 63: Emergency Lights
Article name | Manufacturer | Luminous Flux | Connected Load
 |  | Lm | Watt
Emergency downlight EM120B | PHILIPS | 180 | 4
TCW060 2x36W 2H FLUORESCENT LAMP | PHILIPS | 3906 | 72
EM120B
TCW060

## Slide 64: Emergency Light

## Slide 65: Main Distrubiton Boards Locations

## Slide 66: Sockets Plans
Distribution sockets in GF

## Slide 67: The table shows the electrical load of power, lighting and speakers system in the building
Phases | Floors | D.B | Normal Load | Light Load | Total Power | I Load | I C.B | I cable | C.B | Cable (IEC) | # of power branch | # of light branch
 |  |  |  |  |  |  |  |  |  |  | 16 A,2.5 mm^2 | 10 A,1.5 mm^2
 |  |  | Watt | Watt | Watt | Amp | Amp | Amp | Amp |  |  | 
1 Phase | GF | D.B 1 | 8000 | 1566.5 | 3655.2 | 18.46 | 21.23 | 24.41 | 30 | (36 A) , 6 mm^2 | 11 | 7
 |  | D.B 2 | 3000 | 4920.5 | 4877.4 | 24.63 | 28.32 | 32.57 | 36 | (50 A) , 10 mm^2 | 5 | 10
 | FF | D.B 1 | 6750 | 1787 | 3956.6 | 19.98 | 22.98 | 26.43 | 30 | (36 A) , 6mm^2 | 9 | 8
 |  | D.B 2 | 14500 | 2132 | 6089.6 | 30.76 | 35.37 | 40.68 | 50 | (66 A) , 16 mm^2 | 23 | 28
 | SF | D.B | 7750 | 1389.4 | 3445.52 | 17.4 | 20.01 | 23.01 | 25 | (28 A) , 4 mm^2 | 11 | 13
3 Phases | Final | M.D.B (IN) |  |  | 22024.32 | 37.181 | 42.76 | 49.17 | 50 | (59 A) , 16 mm^2 | 5 | -

## Slide 68: The table show the electrical load of lighting in the outdoor of the building [M.D.B (OUT)]
Phases |  |  | Light Load | Total Power | I Load | I C.B | I cable | C.B | Cable (IEC)
1 Phase | Outdoor | M.D.B(OUT) | Watt | Watt | Amp | Amp | Amp | Amp | 
 |  |  | 9080.2 | 7264.16 | 36.69 | 42.19 | 48.52 | 50 | (66 A) , 16 mm^2
Units |  | Quantity | Power | Total Power | Total Power
 |  |  | Watt | Watt | Watt
Emergency downlight EM120B |  | 34 | 4 | 136 | 1504
TCW060 2x36W 2H FLUORESCENT LAMP |  | 19 | 72 | 1368 | 
Doors | W = 4.65m | 2 | 745.7 | 1491.4 | 4847.2
 | W = 5.65m | 6 | 559.3 | 3355.8 | 
The table shows the electrical load of emergency lighting and doors [M.D.B(IN)]

## Slide 69
Total Power for Generator | W | KW | Amp | VA | KVA | KVA
 | 44640 | 44.64 | 75.45 | 49658.44 | 49.66 | 50
Total Power | W | KW
 | 164213 | 164.21
Units |  | Units | Power | Total Power | I Load | I C.B | I cable | C.B |  | Cable (IEC)
 |  |  | Watt | Watt | Amp | Amp | Amp | Amp |  | 
Elevators |  |  | 9000 | 128572.9 | - |  |  |  |  | 
HVAC Outdoor | Single |  | 35168.5 |  |  |  |  |  |  | 
 | Double |  | 84404.4 |  |  |  |  |  |  | 
Phases | 3 Phase |  |  | 128572.9 | 217.05 | 249.61 | 287.05 |  | 400 | -
 | 1 Phase |  |  | 42857.63 | 68.73 | 79.04 | 90.9 |  |  | (93 A ) , 25 mm2
The table shows the electrical load of Elevator & HVAC system in the building [M.D.B (Elevator & HVAC)]

## Slide 70
Mechanical System
Manholes on the site

## Slide 71
Manholes Calculations
Table of Manholes (Black) |  |  |  | 
Depth | Invert level | Top Level | L (m) | MH's
0.6 | 102.4 | 103 | 0 | 1
0.61 | 102.39 | 103 | 1.17 | 2
0.67 | 102.33 | 103 | 6.08 | 3
0.7 | 102.3 | 103 | 3.26 | 4
0.78 | 102.22 | 103 | 7.86 | 5
0.82 | 102.18 | 103 | 4.23 | 6
0.89 | 102.11 | 103 | 7.49 | 7
0.96 | 102.04 | 103 | 6.95 | 8
1.05 | 101.95 | 103 | 8.73 | 9
1.17 | 101.83 | 103 | 11.89 | 10
1.3 | 101.7 | 103 | 12.67 | 11
1.44 | 101.56 | 103 | 13.78 | 15
0.6 | 102.4 | 103 | 0 | 12
0.68 | 102.32 | 103 | 8.09 | 13
0.76 | 102.24 | 103 | 8.33 | 14
0.9 | 102.1 | 103 | 13.64 | 15
Table of Manholes (Gray) |  |  |  | 
Depth | Invert level | Top Level | L (m) | MH's
0.6 | 102.4 | 103 | 0 | 1
0.64 | 102.36 | 103 | 4.47 | 2
0.76 | 102.24 | 103 | 12.27 | 3
0.8 | 102.2 | 103 | 4.28 | 4
0.94 | 102.06 | 103 | 13.63 | 5
1.07 | 101.93 | 103 | 12.65 | 6
1.21 | 101.79 | 103 | 13.75 | 7
1.35 | 101.65 | 103 | 13.6 | 8
1.43 | 101.57 | 103 | 8.39 | 15
0.6 | 102.4 | 103 | 0 | 9
0.64 | 102.36 | 103 | 3.95 | 10
0.67 | 102.33 | 103 | 2.68 | 11
0.77 | 102.23 | 103 | 10.32 | 12
0.79 | 102.21 | 103 | 1.65 | 13
0.89 | 102.11 | 103 | 10 | 14
0.98 | 102.02 | 103 | 8.93 | 15
T(w) CM) | T(b) CM) | H (CM) | Փ (CM)
7.5 | 12 | 50-100 | 60
12 | 12 | 100-150 | 80
14 | 13 | 150-250 | 100
14 | 14 | >250 | 120

## Slide 72
Pipes Diameter
Fixture | D | S | Pipe
Sewer | 2" | 1% | PVC
Drainage | 4" | 1% | 
Stack | 4" | 0% | 
Drainage between MH's | 6" | 1% | 

## Slide 73
Water Supply
The fresh water consumption for the fireman
= (80 L/day/person )
for the staff = (15 L/day/person )
Daily Demand = (40×80 ) +(6×15 )
= 3200 + 90 = 3290 L/day = 3.29 ̴ 3.5 L
We will need 3 tanks ( 1 , 1 , 1.5 ) L
Block 1 ( 1 L)
Block 2 ( 1 , 1.5 )L

## Slide 74
Fixture Units & Collectors
Fixture Units
Collectors
Floors | No. of Collectors(Fresh)
GF | 1
FF | 4
SF | 1
 | Floors | Wfu's | Demand (gpm)
Vertical | all | 176 | 63
Horizontal | GF | 18 | 14
 | FF | 138 | 14
 | SF | 20 | 14

## Slide 75
Pipe Diameters
 | Pipes | Loss
Vertical | 2.5'' | 3.53
Horizontal | 2'' | 0.38
Branch | 1'' | 0.03
∑ |  | 3.94

## Slide 76
Elevator

## Slide 77: HVAC system
The system that was used is VRF system with cassette units and the maximum cooling load equal 119.6 kW.
The components of this system is from YORK company.
1-Way Cassette units with a capacity of 1.76 kW and 4-Way Cassette units with a capacity of 7 kW.
Single unit system with a capacity of 35.17 kW and double module system with a capacity of 84.4 kW.
We used 5 change over boxes: 4,8 and 12 port.

## Slide 78: HVAC system
The distribution of the cassette units in the first floor:
Zone | Design Capacity (kW) | Design Capacity (ton) | Model | Design flow rate (m3/min) | Num. of cassette units
Bedroom1 | 2.59 | 0.74 | 1-Way Cassette Indoor Unit | 10.1 | 2
Bedroom2 | 4.28 | 1.22 |  | 17 | 3
Bedroom3 | 3.18 | 0.9 |  | 14.3 | 2
Bedroom4 | 3.17 | 0.9 |  | 13.1 | 2
Bedroom5 | 3.38 | 0.96 |  | 14 | 2
Study room | 3.35 | 0.95 |  | 12.4 | 2
Bedroom6 | 2.42 | 0.69 |  | 9.7 | 2
Dining Room | 16.58 | 4.71 | 4-Way Cassette Indoor Unit | 31.8 | 3
Corridor 1 | 7.15 | 2.03 |  | 26.5 | 1
Kitchen | 2.58 | 0.73 | 1-Way Cassette Indoor Unit | 9.4 | 2
Corridor 2 | 0.81 | 0.23 |  | 3 | 1
Theater | 13.23 | 3.76 | 4-Way Cassette Indoor Unit | 40.7 | 2
First Aid Room | 2.01 | 0.57 | 1-Way Cassette Indoor Unit | 7.6 | 2
Corridor 3 | 2.1 | 0.6 |  | 7.1 | 2

## Slide 79: Speaker system
The types of speakers used in the station:
Cornered Audio C6 speaker
The G2 OmniAlert Strobe Speaker
The G2 Illuminated Speaker

## Slide 80: Fire & Safety Design
07

## Slide 81
The symbols for the detection and notification system:
The symbols of the suppression system in the plans:
Firefighting plan for the first floor:

## Slide 82
The different types of the extinguisher in the station:
Space | Extinguisher type
Office | CO2 & water fire extinguishers
Theater | CO2, DCP & water fire extinguishers
Bedroom | CO2, DCP & water fire extinguishers
Kitchen | CO2 & K-type fire extinguishers
Dining Room | CO2 & water fire extinguishers
Parking | CO2 & DCP fire extinguishers
Gym | DCP & water fire extinguishers
The emergency lights and signs & the detectors used in the station:

## Slide 83
Reflected false ceiling for first floor:

## Slide 84: Quantity Surveying & Cost Estimation
08

## Slide 85
Total area of building = 2519.37 m2
Total cost of the project = 10316978 NIS
Cost / Area = 10316978/2519.37 = 4095 NIS/ m2
Items | Total Cost
Earth works | 150939.4
Structural works | 4827359.3
Site works | 1309814.7
Finishes works | 2725746.8
Fire & Safety works | 162268.2
Electrical works | 269197.1
Mechanical works | 433311.3
HVAC works | 438341.2
The total cost for each work of the station:

## Slide 86
Chart: 
| Earth works | Structural works | Site works | Finishes works | Safety works | Electrical works | Mechanical works | HVAC works
المبيعات | 1.46 | 46.8 | 12.7 | 26.42 | 1.57 | 2.61 | 4.2 | 4.25
Percentage for each work from total cost of the station:

## Slide 87: Thanks for your Attention