## Slide 1: Environmental Cars Exhibition (Redesign)
Prepared by:
Ghazal Jamus Noor Qarttalo Taqwa Odwan
Graduation Project II
2015 / 2016
Supervised by:
Dr. Muhannad Hajj Hussein
An-Najah National University
Faculty Of Engineering
Building Engineering Department

## Slide 2: Outlines:
Architectural Design
Site Analysis
Introduction
Environmental Design
Structural Design
Mechanical And Safety Design
Quantity Survey And Cost Estimation
Electrical Design

## Slide 3: Introduction:
The suggested design for our project is one of a student work of the third year of architectural department, who made this design for a location in Tulkarm.
During our project we modified the
selected design (redesign the model)
In order to be suitable for the selected
site in Nablus city.

## Slide 4: Site Analysis:

## Slide 5: Architectural Design:
Redesign Process

## Slide 6
Adaptation and Reorientation:
3rd year student project on his own site 3rd year student project on our new site

## Slide 7: Spaces Distributions:

## Slide 8
Circulations:
Replacing hydraulic elevator with ramps for cars motion
Replacing the stairs with ramps for people motion

## Slide 9
Building Levels:

## Slide 10
Environmental Design:
Environmental Design
and Analysis

## Slide 11: Shading Devices

## Slide 12
Showrooms building:

## Slide 13
Exterior display:

## Slide 14
Cars Parking:

## Slide 15: Teras:

## Slide 16
Daylight Factor (DF%)

## Slide 17: DF%
- In terms of DF% and by using Ecotect simulation program we analyzed four models:
Scenario “4” | Scenario “3” | Scenario “2” | Scenario “1”
New design-proposed glass(with shading) | New design-proposed glass (without shading) | New design-actual glass (without shading) | Actual design-Actual glass

## Slide 18: DF%:
Space description | Scenario “1” | Scenario “2” | Scenario “3” | Scenario “4” | Recommended DF factor (%)
Picture |  |  |  |  | 
Director office | N/A | 3.9 | 4.58 | 4.58 | 3.5-8.8
Showroom (GF) | 7.13 | 8.67 | 4.04 | 4.04 | 3.5-5.9
Showroom (F1) | N/A | 14.76 | 11.93 | 4.83 | 3.5-5.9
Showroom (F2) | N/A | 14.68 | 10.75 | 4.64 | 3.5-5.9
Showroom -Entrance | N/A | N/A | 4.91 | 4.91 | 3.5-5.9

## Slide 19
Thermal Analysis

## Slide 20
Ceiling layers and properties
We defined all the materials for walls, partitions, floors, ceiling, roof, and glass in Ecotect Analysis 2011 program:
Glass layers and
properties

## Slide 21
External wall layers
and properties
Partition layers
and properties

## Slide 22: Monthly heating and cooling loads:
By analyzed the first showroom floor using mixed mode system:
 | Total (Wh) | Total Cooling (Wh) | Total Heating (Wh) |  | Scenario #
 | 51665216 | 46999928 | 4665289 | Total (Wh) | Scenario “1”
 | 75510 | 68692 | 6818 | Per (m2) | 
 | 684.215 |  |  | Floor Area (m2) | 
 | 24521220 | 24260066 | 261153 | Total (Wh) | Scenario “2”
 | 63774 | 63094 | 679 | Per (m2) | 
 | 384.505 |  |  | Floor Area (m2) | 
 | 18008536 | 17988958 | 19578 | Total (Wh) | Scenario “4”
 | 46836 | 46785 | 51 | Per (m2) | 
 | 384.505 |  |  | Floor Area (m2) | 

## Slide 23: Mixed mode system Vs. full air conditioning system:
 | Total (Wh) | Total Cooling (Wh) | Total Heating (Wh) |  | Scenario “4”
 | 18008536 | 17988958 | 19578 | Total (Wh) | Mixed Mode Ventilation System
 | 46836 | 46785 | 51 | Per (m2) | 
 | 384.505 |  |  | Floor Area (m2) | 
 | 35917888 | 35899944 | 17944 | Total (Wh) | Full Air Conditioning System
 | 93413 | 93367 | 47 | Per (m2) | 
 | 384.505 |  |  | Floor Area (m2) | 

## Slide 24: Solar System

## Slide 25
Photovoltaic cells (PV)

## Slide 26: Acoustical Analysis

## Slide 27: RT60
Frequency (Hz) | Total absorption | Sabine (RT60) | NOR-ER (RT60) | MIL-SE (RT60)
63 | 1377.299 | 0.22 | 0.72 | 1.27
125 | 1401.764 | 0.22 | 0.53 | 1.20
250 | 1393.417 | 0.22 | 0.22 | 1.04
500 | 1334.665 | 0.23 | 0.21 | 1.16
1000 | 1330.379 | 0.23 | 0.21 | 1.13
2000 | 1323.240 | 0.23 | 0.21 | 1.02
4000 | 1313.288 | 0.23 | 0.21 | 1.05
8000 | 1342.251 | 0.23 | 0.22 | 1.07
16000 | 1342.251 | 0.23 | 0.22 | 1.06
Volume: 1926.460 m3 Surface Area: 2923.465 m2 Occupancy: 19 (19 x 100%) Optimum RT (500Hz - Speech): 0.89 s Optimum RT (500Hz - Music): 1.52 s |  | Volume per Seat: 101.393 m3 Minimum (Speech): 4.191 m3 Minimum (Music): 8.017 m3 Most Suitable: Millington-Sette (Widely varying) |  | 

## Slide 28
STC for walls STC for Partition
STC and IIC for ceiling
STC and IIC:

## Slide 29: Video

## Slide 30: Structural Design:
Two structural systems were used in the project:
Composite Steel structure
Concrete Structure.

## Slide 31: Composite Steel structure:
Columns Distribution:

## Slide 32: Composite Steel structure:
Steel Frames and Solid slab is used.
Solid slab thickness = 12 cm
Distance Between Girder 1.1m

## Slide 33: Composite Steel structure:
Materials Design Data:
A36 steel with yielding strength (Fy) = 250 Mpa and ultimate strength (Fu) = 400 Mpa
Concrete with Fc' = 24 Mpa
Metal sheet with weight of 32 kg/m2
E70xx welding material, with strength F =480 Mpa.
Loads:
Loads Type | Value
Live | 5 KN/m2
SID | 3.5 KN/m2
Snow | 1.5 KN/m2
Wind For Roof | 0.269 KN/m2

## Slide 34: Soil Type Sc Location: Nablus → Zone: 2B → Z = 0.2 Cv = 0.32 Ca =0.24 I =1 R = 5.5
Seismic Design Data:

## Slide 35
3D – Model
Block C (Show rooms)

## Slide 36: 3D – Model Compatibility Check:

## Slide 37
Equilibrium Checks:
Loads | ETABS- Results | Manual Results | Error
 | 3600.584KN | 3607.8 KN | 0.22 % < 5 %
SID load | 3422.5551KN | 3416.61 KN | 0.15% < 5 %
Beams Number | ETABS- Results | Manual Results | Error %
Main Beam | 160.25 | 178.2 | 10 % ≤10%
Main Beam | 134.87 | 143.4 | 5.9 %≤10%
Beams Moment Checks:

## Slide 38: Design Stage:
Slab Design:
Steel Section used:
← Columns H400X262
Main Beams IPE500V →

## Slide 39
Design Stage:
Connections Design:
Base Plate connection

## Slide 40
Design Stage:
Connections Design:

## Slide 41: Design Stage:
Connections Design:
Column – column connection
Beam – Column connection

## Slide 42: Design Stage:
Beam – Girder connection
Connections Design:

## Slide 43: Fire Proofing Material:
The material used is Intumescent Coatings
Coatings is applied Off site.

## Slide 44
Concrete structure:
Columns Distribution:
Maintains Building

## Slide 45
Concrete F`c For Beams, Columns, Shear walls and Footing = 28 Mpa
Concrete F`c for slab = 24 Mpa
Bearing Capacity For Soil 254 Mpa.
Concrete structure:
For Block A design:
Design Data:

## Slide 46
Material
Reinforced concrete
Gypsum board
Light weight block
Light weight block
Sand
Aggregate
Polystyrene
Mortar
Tile
Materials used:

## Slide 47: Loads Used for Concrete blocks
Load type | Basement floor | Ground floor | First floor | Roof
Live | 5 KN/m2 | 5 KN/m2 | 4 KN/m2 | 3 KN/ m2
SID | 3.5 KN/m2 | 3.5 KN/m2 | 3.5 KN/m2 | 3.5 KN/ m2
Snow | 0 | 0 | 0 | 1.5 KN/ m2

## Slide 48: Preliminary Design For Block A:
Columns:
C 40 X60 cm
Beams:
Main Beams 60 X 40 cm
Secondary Beams 40 X 30 cm
slab
Solid slab thickness is 25 cm
Ribbed slab thickness is 30 cm

## Slide 49: 3D – Model :

## Slide 50: 3D Model – Compatibility Check:

## Slide 51: Equilibrium Check:
Loads | ETABS- Results | Manual Results | Error
Dead Load | 10336.557KN | 10413.6 Kn | 0.74% < 5 %
Live load | 4321.6566KN | 4461.204 KN | 3.67 % < 5 %
SID load | 11272.6312KN | 10158.645 KN | 3.1 % < 5%
Error = ( ( Manual – ETABS Load ) / Manual Load ) X 100% < 5%

## Slide 52
Beam Internal moment Check:
Beam span number | Manual moment (KN.m) | E-Tabs moment (KN.m) | Error %
Span 1 | 72.56 | 73.1 | 0.74%≤10%
Span 2 | 75 | 74.67 | 0.44%≤10%
Span 3 | 56.71 | 56.37 | 0.6%≤10%
Span4 | 26.67 | 28 | 4.9%≤10%

## Slide 53: Design Stage:
Typical Solid Slab Reinforcements in X – Direction For Block A:

## Slide 54: Design Stage:
One – Way Ribbed Slab Reinforcements in X – Direction For Block A:

## Slide 55: Design Stage:
Beams Reinforcements:

## Slide 56: Design Stage:
Column Reinforcements:

## Slide 57: Design Stage:
Shear walls Reinforcements:
Boundary Detailing

## Slide 58: Design Stage:
Wall Footing Detailing:
Isolated Footing Detailing :

## Slide 59: Mechanical Design

## Slide 60: HVAC system
Duct system
Slot and ceiling diffusers

## Slide 61
Zone | Number of diffusers
Ground floor showroom | 25
First floor showroom | 20
Second floor showroom | 20
Entrance | 26
Ramps | 26
Number of diffusers for each space in car show room building
The main duct size = 25x38 cm
For all branches , duct size = 15x26 cm
The diffusers size = 15x15 cm

## Slide 62: Water Supply system
. Cold water
. Clean Water supply ( from municipality)
. Recycled Water
. Storm water
. Domestic Hot water

## Slide 63
Water supply design
Maintenance building
First floor
Administration building
Second floor

## Slide 64
Evacuated tube collectors are used for heating water using solar energy.

## Slide 65: Plumping system:
Ground floor – maintenance building
Black water
Gray water

## Slide 66
External plumping system strategy

## Slide 67: Storm water drainage system

## Slide 68: Electrical Design

## Slide 69: Artificial Lighting
The simulation analysis and design by “DIALux Evo”

## Slide 70: Reception hall
Showroom department -
Uo | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.80 | 400 | 400 | 20

## Slide 71
Ground floor showroom
Uo | UGR | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.75 | 19.4 | 459 | 400 | 79

## Slide 72: First floor showroom
Uo | UGR | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.76 | 24 | 444 | 400 | 76

## Slide 73: Second floor showroom
Uo | UGR | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.76 | 24 | 423 | 400 | 56

## Slide 74: Administration department
Reception and waiting Room
Uo | UGR | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.73 | 17.4 | 341 | 300 | 14

## Slide 75: Account office
Uo | UGR | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.80 | 10.4 | 446 | 300 | 2

## Slide 76: Maintenance department
Painting Both
Uo | UGR | Targeted Lux (avg.) | Recommended Lux | No. of Luminaires
0.70 | 20.3 | 1020 | 1000 | 6

## Slide 77: Sound reinforcement System
Distribution of loudspeakers in the showroom- first floor
Type of used loudspeaker- Control 322C

## Slide 78
Fire fighting systems
Fire hose cabinet
Co2 level sensor
Fire Sprinkler
Safety design

## Slide 79: Fire Sprinkler system
3.06
3.29
4.50

## Slide 80: Quantity Survey and Cost Estimation

## Slide 81: Steel Structure Quantity survey:
Showroom building- Block C total cost = 968563.86 ₪
Item | Unit | Quantity (Unit) | Total Cost ₪
Steel sections | Ton | 125.85 | 755146.₪
concrete works | CM | 505.073 | 161623.3₪
Reinforcements Steel | Ton | 20.89 | 58478.14.₪

## Slide 82
work | unit | Quantity (unit) | Total Cost (₪)
Earth work | CM | 18118 | 305781₪
concrete works | CM | 968.1 | 309792₪
Form works | SM | 4642.1 | 116053₪
steel works | Ton | 395.8 | 1108246.₪
Block | SM | 2526.4 | 63160₪
Concrete Structure Quantity survey:
Total Cost for maintenance building (construction without finishing) = 1903032 ₪

## Slide 83: Showroom envelope quantity survey:
Item | Unit | Quantity (Unit) | Cost | Total Cost ₪
Glass | m2 | 688.82 | 800 | 551056₪
Perforated panels | m2 | 2444.5 | 304 | 743128₪
Aluminum sheets | m2 | 2983 | 50 | 149150₪
Total |  |  |  | 1443334₪
Project Total Cost = 4,314,930 ₪

## Slide 84
We Are So Tired…
Just Give Us an
(A)
Please……..