## Slide 1
Mahde Soboh
Tahreer Sabah
Isalam Taqateq
Shaima’ Suliman
3D Structural Dynamic Evaluation of AL-Arz Ice Cream factory

## Slide 2
Outline
Ch1
Introduction
Ch2
Revision of static evaluation
Ch3
Dynamic evaluation

## Slide 4
Project description
1208.50 m2
180.80 m2
425.00 m2
644.75 m2
1663.50 m2
Basement

## Slide 5
Architectural Plan

## Slide 6
Site and Geology
The office area
310 kN/m2
The factory area
300 kN/m2

## Slide 7
Codes and Standards
ACI 318-08: For reinforced concrete structure design.
IBC 2009: For load determination.
UBC-97: For dynamic design.

## Slide 8
Material
Concrete
Reinforcement Steel
Fy=420MPa
Unit weight= 25kN/m3
fc`= 28 MPa
Es = 200GPa

## Slide 9
Loads
Superimposed dead load
Building | Super imposed dead kN/m2
Factory | 2.25
Offices | 2.27 ( One-way) 1.65 (Two-way )
Live load
Zone | Live load kN/m2
Basement slab (machine zone) | 11
Basement slab (refrigerators zone ) | 13
Repeated slab | 8
Offices | 4

## Slide 10
Loads combinations
According to "ACI 318-08 9.2.1", the load combinations that are used in the design are:
Wu= 1.4 D
Wu= 1.2 D + 1.6 L
Wu= 1.2D.L + 1.0L.L ± 1.0E
Wu= 0.9 D ± 1.0 E

## Slide 11
Structural system

## Slide 12
The selected zones

## Slide 13
Zone B

## Slide 14
Zone D

## Slide 15
Preliminary evaluation
We checked Beam, Column, and slab
Moment reinforcement
Shear reinforcement
Dimensions
OK

## Slide 17
Cases of loading for Zone B

## Slide 18
Compatibility of structural model
Zone B
Zone D

## Slide 19
Equilibrium
Load type | Hand results kN | SAP results kN | Difference %
Dead | 41960.7 | 42652.7 | 1.65
S.I.D | 9135 | 9154.215 | 0.21
Live | 34220 | 34291.98 | 0.21
Load type | Hand results kN | SAP results kN | Difference %
Dead | 17899.5 | 18634.2 | 4.1
S.I.D | 2698.12 | 2694.15 | 0.15
Live | 5028 | 5100.98 | 1.45
Zone B
Zone D

## Slide 20
Stress Strain
Value from hand calculation (kN.m) | Value from SAP (kN.m) | Difference %
1369.8 | 1347.12 | 1.7
Value from hand (calculation( kN.m | Value from SAP (kN.m) | Difference %
246.50 | 244.10 | 0.93
Zone B
Zone D

## Slide 21
Evaluation of slabs for block B
Slab thickness for Shear. OK
Evaluation of slab for resisting bending moment. OK
Long term deflection. ∆ Long term = ∆ L + λ∞ x ∆ D + λt x ∆ SL = 17.3 mm The allowable deflection = = = 22.7 mm

## Slide 22
Evaluation of slabs for block D
Slab thickness for Shear. OK
Evaluation of slab for resisting bending moment. OK
Long term deflection. ∆ Long term = 7.12 < ∆ allowable = 26.60 mm OK

## Slide 23
Evaluation of beams

## Slide 24
Evaluation of columns

## Slide 26
Implementation of RVS for block B

## Slide 27
Verifying and updating the building identification information

## Slide 28
Sketching the Plan and Elevation Views

## Slide 29
Determining soil type

## Slide 30
Determining and documenting occupancy

## Slide 31
Recording Score Modifiers
-0.4 Less than 2

## Slide 32
Implementation of RVS for block D
-0.9
-0.7
0.3
yes

## Slide 34
Seismic Design Category SDC
SDC
C
intermediate

## Slide 35
Check type of structural Detailing
Beam

## Slide 36
Beam
Bottom steel at face of joint ≥ 1/3 top steel at face of joint:
Left joint >>> Achieved.
Right joint >>> Not achieved.
Bottom or top steel at any section ≥ 1/5 top steel at face of joint >>> Not achieved.

## Slide 37
Beam
Stirrups shall be computed based on shear force Vu and shall have a maximum spacing as shown in the figure.
S1 >>> Not achieved.
S2 >>> Achieved.

## Slide 38
Beam
Bottom steel and top steel should be developed ld in the column.
For bottom bars >>>
Not achieved.
For top hooked bars >>> Not achieved.

## Slide 39
Check type of structural Detailing
Lap splice of bars shall be used at mid-height of the column with lap splice length, ls = 1.3 ld.
Not achieved

## Slide 40
Check type of structural Detailing
Column
Stirrups shall be computed based on shear force Vu and shall have a maximum spacing as detailed in the figure.
So >>> Achieved
S1 >>> Achieved

## Slide 41
The result of Check type of structural Detailing
Block D
Block B
Do not meet the requirements of UBC-97 for intermediate structural detailing
&

## Slide 42
Analyze the blocks under the effect of earthquake
Before get the SAP result we should check the code requirement
Mass Source
Modal Mass Participation ratio

## Slide 43
Mass Source

## Slide 44
Modal mass participation ratio Block D

## Slide 45
Modal mass participation ratio Block B

## Slide 46
Periods
SAP
Rayleigh

## Slide 47
Period from SAP for Block B
In Y- direction

## Slide 48
Period from manual calculations (Rayleigh method) for Block B
T (Rayleigh) =

## Slide 49
SAP result VS Rayleigh result for Block B
In Y- direction
SAP
2.277sec
Rayleigh
2.584 sec
2.283 sec
0.26%
Error %
2.567sec
0.66%
X -direction
Y -direction

## Slide 50
SAP result VS Rayleigh result for Block D
In Y- direction
X-direction
Ray=0.201
SAP=0.197
ASP=0.314
Ray=0.326
Y-direction
Error % =2
Error % = 3.8

## Slide 51
Response Spectrum Analysis
In Y- direction

## Slide 52
UBC-97 Factors
In Y- direction
value | Factors
0.2 | Zone
C | Soil Classification
0.24 | Seismic coefficient Ca
0.32 | Seismic coefficient Cv
5.5 | Determine response modification factor (R)
1 | Determine occupancy type (Importance Factor I)

## Slide 53
Response spectrum function definition
In Y- direction

## Slide 54
load cases
In Y- direction
Eh1 = Ex +0.3 Ey
Eh2 = 0.3 Ex + Ey
Ev = Ez

## Slide 55
Base Shear (V) from response spectrum
In Y- direction

## Slide 56
Equivalent Static check
w
𝑣=(𝐶𝑣 𝐼)/(𝑅 𝑇) w
Method B
T= T (Rayleigh)
X-direction
2.283 sec
Y-direction
2.584 sec
Method A
Method A
𝑇=𝐶𝑡ℎ^((3/4))
X-direction
0.944 sec
Y-direction
0.944 sec
Method B
T= T (Rayleigh)
X-direction
2.283 sec
Y-direction
2.584 sec
X-direction
0.944 sec
Y-direction
0.944 sec
Note: 2.283 > 1.4x0.944 = 1.32 sec.
      2.584>1.4x0.944 = 1.32 sec.
So , use T = 1.32 sec.

## Slide 57
The manual value of Equivalent Static
In Y- direction
V min
1502 kN
0.11 𝐶𝑎 𝐼 𝑊= 1502 kN
V
w = 2508 kN
(𝐶𝑣 𝐼)/(𝑅 𝑇) w = 2508 kN
V max
W = 6205 kN
(2.5 𝐶𝑎 𝐼)/𝑅 W = 6205 kN
V min
V
V max

## Slide 58
Response spectrum base shear VS Equivalent static base shear
In Y- direction
Equivalent Static | Response Spectrum | Direction
2507.47 | 1306.76 | X
2507.47 | 1171.23 | Y
2507.47 | 122.96 | Z
Note: in UBC97, for all regular structures, the base shear from response spectrum analysis shall be not less than 90% of the base shear determined by equivalent static method (2256.73).

## Slide 59
Modify the scale factor
In Y- direction

## Slide 60
Final SAP Results for Block B
In Y- direction

## Slide 61
Final SAP Results for Block D
In Y- direction

## Slide 62
Comparison between Static and Dynamic Results Block B
Slab
Envelop Combination | Static Combination | Internal Forces
42 kN | 39.7 kN | V13
46.2 kN.m | 45.9 kN.m | M11 (+ Ve )
50.96 kN.m | 49.1 kN.m | M11 (-Ve )

## Slide 63
Comparison between Static and Dynamic Results Block B
Beam

## Slide 64
Comparison between Static and Dynamic Results Block B
Column

## Slide 65
Comparison between Static and Dynamic Results Block D
Slab.
The static design govern.
Beam.
  That the increasing in M (-Ve), M (+Ve), shear and torsion are not considerable.
Column.
  We note that the values of Pu is increased in all columns but the values of M2, M3 and shear does not increased considerably.

## Slide 66
Check Drift for Block B
ΔM = 0.7 × R × ΔS
ΔS | Floor number
4.5 | 5th floor
7.2 | 4th floor
9.8 | 3rd floor
12.3 | 2nd floor
15.3 | 1st floor
28.8 | Ground floor
14.2 | Basement floor
ΔM = 109 mm < Maximum limitation = 0.02 ×story highet= 113mm OK.

## Slide 67
Check Drift for Block D
ΔM = 0.7 × R × ΔS
ΔS (mm) | Floor number
1.7 | 3rd floor
1.8 | 2nd floor
1.6 | 1st floor
1.4 | Ground floor
ΔM = 7mm < Maximum limitation = 0.02 ×story highet= 92mm OK

## Slide 68
Check building separation

## Slide 69
The required separation between Blocks
In Y- direction
∆ΜΤ= √(〖(Δ𝑀1)〗^(2 )+〖(Δ𝑀2)〗^2 )
Between Blocks A&B
50 cm
Between Blocks A&D
31 cm
Between Blocks A&B
50 cm
Between Blocks A&D
31 cm
The separation used = 3 cm !!!

## Slide 71
Retrofitting for seismic separation (Block A)

## Slide 72
Retrofitting for seismic separation (Block B)

## Slide 73
The result of retrofitting for seismic separation
The required
separation = 2 cm
The used
separation = 3 cm
But, this solution dose not work, Why ??!!

## Slide 74
Retrofitting of columns
Load of column
Pu = 10036 kN.
In X-direction of column
M3 (bottom) = -956 kN.m.
M3 (top) = -311 kN.m.
In Y-direction of column
M2 (bottom) = -1260 kN.m.
M2 (top) = -108 kN.m

## Slide 75
Retrofitting of columns
Check Slenderness Effect
  The Slenderness effects can be neglected in both directions X and Y.

## Slide 76
Retrofitting of columns
Design column for axial and moment .
  In X-direction ρ = 1%>>> Use 32Ø18
  In Y-direction ρ = 1%>>> Use 32Ø18

## Slide 77
Retrofitting of columns
Design column for shear.
Vu = max
Vu from design combination include 3.0 E
l

## Slide 78
Retrofitting of columns
Design hoops and check spacing.
  Use 3Ø10 hoops (6 legs)
  Max spacing.
  S1 =288 mm
  So =144 mm

## Slide 79
Retrofitting of columns
Final dimensions
Column | Before retrofitting |  | After retrofitting | 
 | Dimensions | Steel | Dimensions | Steel
C1 |  | 24Ø18 |  | 32Ø18
C2 |  | 18Ø16 |  | 24Ø16
C3 |  | 16Ø16 |  | 18Ø16
Column | Before retrofitting |  | After retrofitting | 
 | Dimensions | Steel | Dimensions | Steel
C1 |  | 24Ø18 |  | 32Ø18
C2 |  | 18Ø16 |  | 24Ø16
C3 |  | 16Ø16 |  | 18Ø16

## Slide 80
Retrofitting of columns
Check Splice length and location.
  Ls required = 860 mm
  Lo required = 900 mm

## Slide 81
Retrofitting of columns
How to execute C1 in reality

## Slide 82
Retrofitting of Beam
Load of Beam
Mu-ve (Right) = 1112 kN.m
Mu-ve (Left) = 1025 kN.m
Mu+ve = 502 kN.

## Slide 83
Retrofitting of Beam
Design beam for moment .
Steel Reinforcement | The value of the moment
12Ø25 | Mu-ve (Right) = 1112 kN.m
16Ø20 | Mu-ve (Left) = 1025 kN.m
10Ø18 | Mu+ve = 502 kN.m

## Slide 84
Retrofitting of Beam
Reinforcement for moment.

## Slide 85
Retrofitting of Beam
Verify minimum intermediate detailing requirements.
As+ at face of joint ≥ 1/3 As- at face of that joint. OK
Bottom or top steel at any section ≥ 1/5 max steel at face of either joint. OK

## Slide 86
Retrofitting of Beam
Design beam for shear.
Vu = max
2 Vu from design combination include E
l

## Slide 87
Retrofitting of Beam
Design of hoops and check spacing.
  Use 2Ø10 hoops (4 legs)
  Max spacing.
  S1 =112 mm >>> (use 2Ø10@10cm)
  S2 =295 mm >>> (use 2Ø10@20cm)

## Slide 88
Retrofitting of Beam
Check Ld.
  For top hooked bars = 290 mm.
  For bottom hooked bars = 260 mm.
  For straight top bars = 1200 mm.
  For straight bottom bars = 660 mm.
Available length = 540 mm OK

## Slide 89
Retrofitting of Beam
How to execute B1 in reality.

## Slide 90
Evaluation of Foundations of Block B
Check if we really need mat foundation.

## Slide 91
Evaluation of Foundations of Block B
Checks of mat foundation for.
  Compatibility , OK.
  Deflection Δ allowable > max deflection, OK.
  Stress, The applied stress <qu, OK.
  Punching shear, OK.
  Reinforcement in both direction, OK.

## Slide 92
Evaluation of Foundations of Block D
  Checks of single footing.
  Check the area of the footing based on the allowable bearing capacity of the soil, Not OK.
  Check footing depth for wide beam shear, OK.
  Check footing depth for punching shear, OK.
  Reinforcement, OK.

## Slide 93
Retrofitting of Foundations of Block D

## Slide 94
Design of shear wall

## Slide 95
Design of shear wall
Internal forces and moment.
  M1 (Muy) = 20 kN.m.
  M2 (Mux) = 1600 kN.m.
  F1 (Vuy) = 680 kN.
  F2 (Vux) = 10 kN

## Slide 96
Design of shear wall
Check shear in X- direction. ΦVc = 0.75(1/6))(200-40)(4200)/1000 = 444 kN > 10kN ,, OK.
Design for shear in Y- direction.
  Use 2Φ12 mm @ 250 mm C/C.
Design for moment around Y- axis.

## Slide 97
Design of shear wall
Design for axial force and moment around X- axis.

## Slide 98
Design of shear wall
Use 11Φ14 mm/m on each face.