## Slide 1: Graduation Project 2 Assessment and Potential of using Passivated Emitter and rear cell (PERC) in Palestine
Supervisor: Eng. Ramez Khaldi
Students:
* Belal Bazzari * Abdallh Shawhnee

## Slide 2: Content:
Introduction
Energy types
PERC Cell and Advantages
Efficiency and Market Share
Methodology
Data Sheet
Devices
Experimental Data
Challenges
Recommendations
Conclusion

## Slide 3: Introduction
The importance of energy.
Palestine is 100% dependent on neighboring countries for fuel, and 90% for electricity.
The percentage of renewable energy from the energy consumed in Palestine is 11.7% .
The percentage of families using solar heaters reached 56% in Palestine.

## Slide 4: Energy types:
Non-renewable sources
Fossil fuels
Natural Gas
Coal
Nuclear energy
Renewable resources
Solar energy
Wind energy
Water energy
Geothermal

## Slide 5: PERC Cell and Advantages
PERC stands for (Passive Emitter and Back Cell) and it is basically a process that adds an extra layer on the back of the solar cell to reflect some of the light photons that manage to pass through the cell back into the cell, thus increasing the overall efficiency. This method takes a standard solar cell and adds an extra layer to the backside. The passivation layer acts as a mirror that reflects the light that has already passed through the plate. This gives the light a second chance to be absorbed by the solar cell, resulting in increased absorption of solar radiation.

## Slide 8: Efficiency and Market Share

## Slide 9: Methodology
The work plan

## Slide 10: Data Sheet
Technology | Model | VOC (V) | ISC (A) | Pmp (W) | η (%)
PERC | TP660M-310 | 40.1V | 9.69 A | 310 | 18..9
AL-BSF | SR 350-72M | 47.24V | 9.56 | 350 | 18.03

## Slide 11: Devices
•Temperature Measurement by Using a thermometer

## Slide 12: Devices
Irradiance & Power Measurements by Using IV-400.

## Slide 13: Experimental Data
Power perc(w/m^2) | Power poly(w/m^2) | Irr perc poly(w/m^2) | Irr poly(w/m^2) | Temp perc(c°) | Temp poly(c°) | Hour | Date
72.70283 | 68.54426 | 360 | 390 | 33.1 | 34.1 | 9 | 2-Oct
114.2473 | 106.6817 | 605 | 587 | 39.9 | 41.1 | 10 | 
141.129 | 130.3887 | 792 | 751 | 56.6 | 57.7 | 11 | 
153.9589 | 140.6961 | 882 | 826 | 50.2 | 51.1 | 12 | 
0 | 0 | 0 | 0 | 0 | 0 | 1 | 
148.4604 | 125.235 | 858 | 758 | 48.5 | 49 | 2 | 

## Slide 14: Temperature Measurement Result
Chart: Average daily temperature
| 44829 | 44830 | 44831 | 44832 | 44833 | 44836 | 44837 | 44838 | 44839 | 44840 | 44843 | 44857 | 44858 | 44864
poly | 45.88 | 50.65 | 44.7 | 52.25 | 42.6667 | 46.6 | 49.9 | 50.175 | 45.05 | 44.7 | 36.9 | 34.9 | 45.8667 | 38.45
perc | 44.32 | 48.975 | 42.9667 | 48.45 | 41.1667 | 45.66 | 48.6 | 48.675 | 43.625 | 43.975 | 34.025 | 32.95 | 44.8667 | 36.3

## Slide 15: Irradiance Measurement Results
Chart: Average daily irradiance
| 44829 | 44830 | 44831 | 44832 | 44833 | 44836 | 44837 | 44838 | 44839 | 44840 | 44843 | 44857 | 44858 | 44864
POLY | 674.4 | 774.25 | 694.3333 | 810.5 | 607.6667 | 662.4 | 728 | 718 | 653.75 | 643.75 | 709.25 | 549 | 706 | 400
PERC | 715.8 | 788.5 | 712.6667 | 877 | 644.3333 | 699.4 | 758 | 775.25 | 707.75 | 696.5 | 740.75 | 582.75 | 769.3333 | 434

## Slide 16: Power Measurement Results
Chart: average daily power
| 44829 | 44830 | 44831 | 44832 | 44833 | 44836 | 44837 | 44838 | 44839 | 44840 | 44843 | 44857 | 44858 | 44864
poly | 118.4321 | 128.4561 | 115.9583 | 142.7576 | 104.2766 | 114.3092 | 127.6401 | 124.5908 | 109.7739 | 114.2834 | 117.891 | 101.7857 | 125.7504 | 74.471
perc | 132.9423 | 148.9186 | 133.594 | 157.0137 | 119.7458 | 126.0997 | 135.8341 | 137.0051 | 129.521 | 124.328 | 137.3106 | 114.7055 | 139.0925 | 80.6452

## Slide 17: Efficiency Measurement Results :
Chart: average monthly effeciency
| sep | oct
poly | 17.2453 | 17.8793
perc | 18.5763 | 18.7568

## Slide 18: Challenges
The IV-400 is not able to give readings for panels with a short-circuit current (Isc) higher than 9.99A, so we had to search for panels with an Isc (short-circuit current), and it was also difficult to find two panels with the same capacity and area, and after a lot of searches we got two plates and we couldn't get the same capacity and area, because of that we compared the power per unit area (w/m^2)

## Slide 19: Conclusion:
Economic analysis proves that this technology has dominated the photovoltaic market for the past four years, and PERC technology has reached its theoretical limit of 24.5% cell efficiency. The results of the experimental study in Palestine (the hot Middle East and North Africa region) proved that this technology adds more energy and efficiency. By studying the factors affecting the efficiency of the photovoltaic cell and analyzing the results that we studied in this project.

## Slide 20: Recommendations
Through the results that appeared in our experience, we recommend the use of PERC panels, due to their efficiency and high energy productivity in the climate of Palestine, and we recommend those who are about to install solar energy panels to make sure that the panels that will be installed are of high efficiency.

## Slide 21: Thanks