## Slide 1: An-Najah National University Faculty Of Engineering Material &Chemical Engineering Department Graduation Project 2
Prepared by:
Dina Faidi
Haneen Madina
Muna khader
Taqwa Hariri
Supervision of Dr. Husni Odeh
Descaling of cooling tower and corrosion protection

## Slide 2: OUTLINE
Introduction
Objective
Methodology
Chemical Analysis
Instrumental Analysis
Results
Feasibility Study
Conclusion

## Slide 3: What is the problem ?
The main problem that scaling in cooling tower system in Aziza Company .

## Slide 4
Principle of cooling tower:

## Slide 5: The aim of this project:
To find solutions to mitigate scale formation and corrosion encountered in cooling towers
To understand the formed deposits

## Slide 6: Description of aziza poultry farms
The farm contains 4 chicken indoor farms each of them has a width=14 m, it’s length= 111m and the height=3.5 m.
Each farm contains 2 sidewalls of cooling ,it’s height =180 cm and it’s length=18 m
12 suction fans
The source of water
Water has collected from arestian wells in auja area
The amount of water is used daily =90-1000cup
Cleaning and maintainance when the farm is evacuated

## Slide 7: Analysis to know what is the deposited salt
Icp
XRD
Flame photometer
Ph meters

## Slide 8: Methodology
Visit the website of Aziza Company
To see the problem are experiencing on the ground .

## Slide 10: Methodology
Research Methodology :
Descaling of cooling tower and corrosion protection project began with searching in scientific articles and several journals for how to What are the causes of the problem of the scaling in the cooling tower and how to get rid of the scaling on the cooling towers and have been studied many scientific articles.

## Slide 11: Methodology
Sampling :
1-Solid Sample
Species of cooling tower conation scaling
Using Hummer to cut and Graind it
Soil Grinder to transfer it to powder
Solid powder sample

## Slide 12: Methodology
Sampling :
2-Liqued water Sample

## Slide 13: Methodology
Sample Analysis :
1-Chemical Analysis.
2-Instrumental Analysis.

## Slide 14: Experimental Part
In last semester was made:
Acidulation experiments:
Determine amount of scaling remove by used Citric acid
Determine amount of scaling remove by used Acetic acid
Base experiments:
Determine amount of scaling remove by used Sodium phosphate solution

## Slide 15: Experimental Part
Determination Check amount of sodium using a flame photometer
cooling tower
Broke the scale from it by use Hammer
grinded it by the soil grilling machine

## Slide 16: Experimental Part Determination Check amount of sodium using a flame photometer
1.004 gr of the grinded scale sample
grinded scale sample
1 ml HNO3
Distillated water to 1000ml

## Slide 17: Experimental Part
Determination Check amount of sodium using a flame photometer
Standard solution of sodium 1000 ppm
10 ml of standard solution

## Slide 18: Experimental Part
Determination Check amount of sodium using a flame photometer
10 ml Sodium stock standard solution
wire out of the device
Flame photometer become yellow

## Slide 19: Experimental Part
Determination Check amount of sodium using a flame photometer
10 ml Sodium sample solution
Flame photometer become yellow
wire out of the device

## Slide 20: Experimental Part
Determination Check amount of Potassium using a flame photometer
cooling tower
Broke the scale from it by use Hammer
grinded it by the soil grilling machine

## Slide 21: Experimental Part Determination Check amount of Potassium using a flame photometer
1.004 gr of the grinded scale sample
grinded scale sample
1 ml HNO3
Distillated water to 1000ml

## Slide 22: Experimental Part
Determination Check amount of Potassium using a flame photometer
Standard solution of Potassium 1000 ppm
10 ml of standard solution

## Slide 23: Experimental Part
Determination Check amount of Potassium using a flame photometer
10 ml Potassium stock standard solution
wire out of the device
Flame photometer become Blue

## Slide 24: Experimental Part
Determination Check amount of Potassium using a flame photometer
10 ml Potassium sample solution
Flame photometer become Blue
wire out of the device

## Slide 25: Experimental Part
Determination amount of Organic compounds
cooling tower
Broke the scale from it by use Hammer
grinded it by the soil grilling machine

## Slide 26: Experimental Part
5 gr of each two samples
Placed both in the furnace for 2hr and 500oC
Determination amount of Organic compounds

## Slide 27: Experimental Part
Determination amount of Organic compounds
One of two samples was weighted
One of two samples was weighted
100 ml of water
The sample was filtered

## Slide 28: Experimental Part
Determination amount of Organic compounds
filter paper was weighed
water remains after filtration used for another test

## Slide 29: Experimental Part
Filter Paper was weighted
Placed it in the furnace for 20min and 500oC
Determination amount of Organic compounds
Filter Paper was weighted after cooled

## Slide 30: Experimental Part
Determination amount of Organic compounds
anther of two samples was weighted
another of two samples
1ml of HNO3 (68%)
1ml of H2SO4 (99.9%)
20 ml of water

## Slide 31: Experimental Part
Determination amount of Organic compounds
The sample was filtered
Heated to form a transparent layer.

## Slide 32: Experimental Part
Determination amount of Organic compounds
filter paper was weighed
water remains after filtration used for another test

## Slide 33: Experimental Part
Test of Electric Conductivity (E.C) for both samples:
water remains after filtration for first sample
measured amount of organic in sample by E.C

## Slide 34: Experimental Part
Test of Electric Conductivity (E.C) for both samples:
water remains after filtration for another sample
measured amount of organic in sample by E.C

## Slide 35: Experimental Part Determination Check amount of Potassium using a flame photometer
5 g of the sample was weighted
grinded scale sample
5 ml HNO3
20 ml of Distillated water
5ml of H2SO4

## Slide 36: Experimental Part
Estimation amount of Silica
The layer above the liquid was removed
Heated to make all the turbidity under the liquid

## Slide 37: Experimental Part
Estimation amount of Silica
Distilled water was added to obtain a transparent layer of the silica
transparent layer was filtered and weighed amount

## Slide 38: Induced Couple Plasma-Mass Spectrometry
We conducted an ICB test for the water used by Aziza Company in cooling towers.
This inspection was done at the Water and Scientific Research Canter.
The ICB test was carried out in order to identify the elements that were not observed and did not appear through the previous tests and were also done in order to know the quantities and proportion of the deposited elements. We put a sample of this water in the ICB device. It may have caused deposits on the cooling towers.

## Slide 39: X-Ray Powder Diffraction
Ttechniques are a set of non-destructive analytical techniques that reveal information about crystalline structure, chemical composition, physical properties of materials and thin films.
These techniques depend on observing the scattered density of the x-ray beam that strikes a sample as a function of the sporadic and scattered angle, polarization, wavelength or energy

## Slide 40: X-Ray Powder Diffraction
How to scan x-ray:
A sample was taken from the cooling towers and grinded and then sent to the American University in Jenin for an X-ray examination.
The sample was placed in the X-ray apparatus to identify the elements and compounds deposited on the roofs of the cooling towers. X-rays were directed towards the sample and During the shape that appeared on the device was known crystals and elements present and quantities.

## Slide 41: Result Result from Chemical Analysis
Result | Unit | Test
720 | Mg/l | Ca
3360 | Mg/l | Na
709 | Mg/l | Mg
5300 | Mg/l | Cl
290 | Mg/l | HCO3
0 | Mg/l | CO3
190 | Mg/l | K
19.8 | Mg/l | NO3
1499 | Mg/l | SO4

## Slide 42: Result Result from Chemical Analysis
Estimation Of Silica
Si =.1661g

## Slide 43: Result Result from ICP
Result | Unit | Analyte
0.03756 | Mg/l | Ag
2.7041 | Mg/l | Fe
0.60568 | Mg/l | Li
20.6985 | Mg/l | Sr
.07596 | Mg/l | Ba

## Slide 44: Result Result from XRD
Chart: X-Ray Pattern of our powder solid sample

## Slide 45: Result Matching between our sample & Gypsum(CaSO4.2H2O) Peak
Chart: X-Ray Pattern of our powder solid sample
2Theta = 11.5
2Theta=20.55
2Theta =23.2
2Theta =28.9
2Theta =33.15

## Slide 46: Result Matching between our sample & Halite(NaCl) Peak
Chart: X-Ray Pattern of our powder solid sample
2Theta =31.9
2Theta=45.3
2Theta=56.5

## Slide 47: Result Matching between our sample & Celestine(SrSO4) Peak
Chart: X-Ray Pattern of our powder solid sample
2Theta =40.45
2Theta=43.15

## Slide 48: Cost analysis
This is a simple study for cleaning cooling tower costs
=cost of cleaning/session*# of times for cleaning
=7*3040=21280NIS
Cost of chemicals for 10 L | 500NIS
1 cube of salt water | .8 nis
Brushing operation(6-8) hrs | 5.5 nis (electricity)
1 cube of drinking water | 27 nis
Cost of pumping water | 5.5 nis
Worker cost | 2500 nis
 | 3040nis/session

## Slide 49: Alternative method
After researching about an alternative way ,Reverese osmis system is the best way to reduce the cost of cleaning and it has a life time about 10 years
It’s cost =42000
Taking into consideration the life time of cooling tower in Jericho only 3 years

## Slide 50: Conclusion
From Chemical Analysis
we found ( Cl =5300Mg/l , Na =3360Mg/l , SO4 = 1499 Mg/l )
From Instrumental Analysis
we found From ICP-MS ( Sr =20.68Mg/L ).
Most Peak we found in from XRD is Gypsum (CaSO4.2H2O) , Halite (NaCl) , Celeite(SrSO4)
The amount of silica is low ,that not cause the problem.
الاشي من الدراسة المالية

## Slide 51
Thank you