## Slide 1: The Analysis And Design Of Beit Furik Water Supply Network
Prepared by: Miriam Tamim
Yamama Mlitat
Under supervision of: Dr. Anan Jayyousi
Graduation project II

## Slide 2: Introduction

## Slide 3: Study Area: Beit Furik

## Slide 4: Location: Beit Furik is a Palestinian town in Nablus Governorate, located approximately 7 km south east of Nablus City.

## Slide 5
Area: The total area is 36663 dunums, while the area of ​​the approved master plan is 4658.36 dunums.
Population: According to PCBS-2017, it had a population of 13,477 inhabitants.

## Slide 6
Water service provider: Joint Services Council with Beit Dajan as well as private sources.
Main water source: One permanent source of water (Beit Furik artesian well). Provided to citizens through the public water network established in 2009.

## Slide 7: Questionnaire Results
The average daily per capita water consumption is 62.28 liters.
Beit Furik is divided into eight regions, where the municipality provides each region (on average) with water every 5-10 days for approximately 3 hours.
Approximately 87% of our sample stated that they order water tankers.

## Slide 8
Chart: Do you have a problem in the access of water to your house?
No Yes | 19 | 11
Questionnaire Results

## Slide 9: Preparation of the input file for waterCAD
AutoCad file of existing network
DXF files
To
Inserted to
WaterCad
Draw
Pipes
Nodes
Reservoir
-Diameter
-Material (CHW )
-Length
-Elevation
-Demand
-Total Head

## Slide 10: Existing Water Network

## Slide 11: Problems of existing water network:
Intermittent Supply
Lack of water resources & inadequacy of water supply
Difficulty of water access to some citizens

## Slide 12: Network Analysis Results
Chart: Node ID
Chart: Pipe ID

## Slide 13: For future considerations, the following assumptions were made:
Design period = 20 years
Domestic consumption for Beit Furik citizens = 100 L/c-d
Physical losses =15%
Domestic consumption = 90% of total municipal consumption
The future designed network will provide continuous supply of water
The Palestinian hourly pattern was used in the design
The recommended values of velocity are (0.3 -3) m/s and the recommended pressure values are (15-100) mH2O

## Slide 14
Demand future= pop future* unit water domestic consumption*
Demand 2039= 24,955 * 0.1* = 3,262.09 m3/day

## Slide 15: Alternative I (Business as usual)

## Slide 16: Alternative I (Business as usual)

## Slide 17: Alternative I (Business as usual)
Chart: Pipe ID
Chart: Node ID

## Slide 18: Alternative I Setbacks
High Pressure Head
Fittings damage
High leakage & wasted water
More maintenance
Expulsion of pipes

## Slide 19: Pressure Zone Definition
Pressure zone is an area bounded by a lower and upper elevation, all of which receives water from a given reservoir and it is usually used when having an elevation difference of more than 120m.

## Slide 20: Alternative II(Pressure Zoning)
648 m AMSL
555m AMSL
535m AMSL
458 m AMSL
Existing Reservoir
Lowest Node
New Reservoir
Separation Level

## Slide 21: New reservoir location was selected based on these factors:
Must be set at an elevation intermediate the elevation difference between the lowest and highest spots in the network
To be placed in an empty area of 0.5 dunums
To be close to the roads network

## Slide 22: Alternative II(Pressure Zoning)
648 m AMSL
555m AMSL
535m AMSL
458 m AMSL
Existing Reservoir
Lowest Node
New Reservoir
Separation Level

## Slide 23
Demand for area #2= *Total Demand
= 0.792107 * 3262.09= 2583.925 m3/day
Demand for area #1= *Total Demand
= 0.207893 * 3262.09= 678.1648 m3/day

## Slide 24: Alternative II(Pressure Zoning)
Chart: 
Chart: 

## Slide 25: New Reservoir Size
Chart: Hour
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cum Supply | 107.6635 | 215.327 | 322.9905 | 430.654 | 538.3175 | 645.981 | 753.6445 | 861.308 | 968.9715 | 1076.635 | 1184.2985 | 1291.962 | 1399.6255 | 1507.289 | 1614.9525 | 1722.616 | 1830.2795 | 1937.943 | 2045.6065 | 2153.27 | 2260.9335 | 2368.597 | 2476.2605 | 2583.924
Cum Demand | 51.6785 | 80.7476 | 109.8168 | 158.2653 | 206.7139 | 400.5082 | 594.3025 | 739.6482 | 884.994 | 991.5808 | 1098.1677 | 1195.0648 | 1291.962 | 1398.5489 | 1505.1357 | 1621.4123 | 1737.6889 | 1931.4832 | 2125.2775 | 2251.2438 | 2377.2101 | 2454.7278 | 2532.2455 | 2583.924

## Slide 26
Business As Usual
Pressure Zoning
Chart: 
Chart: 

## Slide 27
Business As Usual
Pressure Zoning
Cost Consideration
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 28
Business As Usual
Pressure Zoning
A= 130,399 $
P= 107,964 $
A= 81,242.7 $
P= 930,074 $
Cost Consideration

## Slide 29: Conclusion
Pressure zoning is recommended for Beit Furik for these reasons:
Elevation difference more than 120 m (which is 190 m)
40% energy and cost saving
Lower mainenance costs & better management

## Slide 30: Thank you for listening 