## Slide 1: An- Najah National University Optimum design and Performance for Nablus Network
Submitted To :
Dr. Maher Khammash
Prepared By :
Haitham Sharaf
Ahmad Odeh

## Slide 2
ABSTRACT
Project One was to gather initial data for
"Mojair Addin" network and subject it to a
load flow study under its normal condition
(6.6 kV).

## Slide 3: One Line Diagram of Nablus Network

## Slide 4: The following results were obtained: normal condition ( 6.6 kv) :
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Bus100 | 6.600 | 5.9 | 89.4
Bus102 | 6.600 | 5.853 | 88.7
Bus104 | 6.600 | 5.859 | 88.8
Bus178 | 6.600 | 5.805 | 87.9
Bus179 | 6.600 | 5.807 | 88
Bus185 | 6.600 | 5.667 | 85.9
Bus223 | 6.600 | 6.04 | 91.5
Bus225 | 6.600 | 6.009 | 91.1
Bus230 | 6.600 | 6.08 | 92.1
Bus55 | 0.400 | 0.361 | 90.3
Bus8 | 0.400 | 0.364 | 91
Bus132 | 0.400 | 0.371 | 92.7
Bus148 | 0.400 | 0.343 | 85.7
Bus33 | 0.400 | 0.377 | 94.2
Bus79 | 0.400 | 0.339 | 84.7
The following table shows the under voltages on some buses

## Slide 5: Some Of Under Voltage Buses :

## Slide 6: Summary of Total Generation, Loading & Demand :
* Under voltage buses and low power factor are
observed

## Slide 7
PROJECT GOAL
For project II, the voltage level is
increased from 6.6kV to 11kV and is analyzed
under 3 conditions:
1. Max. case.
2. Min. case.
3. Post-fault case.

## Slide 8: Changing the voltage level ( 6.6 -11) kv:
after raising the voltage to 11kV, the
voltage drop was notably decreased and a
slight improvement to the power factor was
observed.

## Slide 9: The following table shows the under voltages on some buses:
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Bus100 | 11.00 | 10.245 | 93.1
Bus102 | 11.00 | 10.217 | 92.9
Bus104 | 11.00 | 10.221 | 92.9
Bus178 | 11.00 | 10.19 | 92.6
Bus179 | 11.00 | 10.191 | 92.6
Bus185 | 11.00 | 10.116 | 92
Bus223 | 11.00 | 10.325 | 93.9
Bus224 | 11.00 | 10.325 | 93.9
Bus225 | 11.00 | 10.308 | 93.7
Bus230 | 11.00 | 10.35 | 94.1
Bus8 | 0.400 | 0.375 | 93.7
Bus132 | 0.400 | 0.377 | 94.3
Bus148 | 0.400 | 0.368 | 91.9
Bus33 | 0.400 | 0.379 | 94.8
Bus79 | 0.400 | 0.366 | 91.5

## Slide 10: Summary of Total Generation, Loading & Demand :

## Slide 11: Maximum Case :
The tap changer of the main
transformer was increased by 10% and
six capacitors were added on the lowest
voltage buses of (600, 4x800, 400 kVAr) in
order to improve the voltages and the power factor.

## Slide 13: The following table shows the over voltages on some buses:
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Bus100 | 11.00 | 11.531 | 104.8
Bus102 | 11.00 | 11.505 | 104.6
Bus104 | 11.00 | 11.508 | 104.6
Bus178 | 11.00 | 11.478 | 104.3
Bus179 | 11.00 | 11.480 | 104.4
Bus185 | 11.00 | 11.419 | 103.8
Bus223 | 11.00 | 11.579 | 105.3
Bus224 | 11.00 | 11.579 | 105.3
Bus225 | 11.00 | 11.565 | 105.1
Bus230 | 11.00 | 11.613 | 105.6
Bus8 | 0.400 | 0.421 | 105.1
Bus132 | 0.400 | 0.423 | 105.7
Bus148 | 0.400 | 0.415 | 103.7
Bus33 | 0.400 | 0.424 | 106
Bus79 | 0.400 | 0.414 | 103.5

## Slide 14: Summary of Total Generation, Loading & Demand :

## Slide 15: Minimum Case :
First, the tap changer was increased by 5%
and the loads were halved (decreased by 50%).
then, 5 capacitors were added of (200, 800,
2x400, 100 kVAr).

## Slide 17: The following table shows the over voltages on some buses:
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Bus100 | 11.00 | 11.254 | 102.3
Bus102 | 11.00 | 11.241 | 102.2
Bus104 | 11.00 | 11.243 | 102.2
Bus178 | 11.00 | 11.228 | 102.1
Bus179 | 11.00 | 11.229 | 102.1
Bus185 | 11.00 | 11.2 | 101.8
Bus223 | 11.00 | 11.3 | 102.7
Bus224 | 11.00 | 11.299 | 102.7
Bus225 | 11.00 | 11.292 | 102.7
Bus230 | 11.00 | 11.322 | 102.9
Bus8 | 0.400 | 0.411 | 102.7
Bus132 | 0.400 | 0.412 | 103
Bus148 | 0.400 | 0.407 | 101.7
Bus33 | 0.400 | 0.412 | 103.1
Bus79 | 0.400 | 0.407 | 101.8

## Slide 18: Summary of Total Generation, Loading & Demand :

## Slide 19: Post-Fault Case:
    In this case, the maximum case was used and the branch with the highest
    apparent power will have its impedance
    (R & X) multiplied by 2.

## Slide 21: The following table shows the over voltages on some buses:
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Bus100 | 11.00 | 11.53 | 104.8
Bus102 | 11.00 | 11.504 | 104.6
Bus104 | 11.00 | 11.507 | 104.6
Bus178 | 11.00 | 11.477 | 104.3
Bus179 | 11.00 | 11.479 | 104.4
Bus185 | 11.00 | 11.418 | 103.8
Bus223 | 11.00 | 11.471 | 104.3
Bus224 | 11.00 | 11.470 | 104.3
Bus225 | 11.00 | 11.457 | 104.2
Bus230 | 11.00 | 11.612 | 105.6
Bus8 | 0.400 | 0.417 | 104.1
Bus132 | 0.400 | 0.423 | 105.8
Bus148 | 0.400 | 0.415 | 103.7
Bus33 | 0.400 | 0.424 | 106
Bus79 | 0.400 | 0.414 | 103.5

## Slide 22: Summary of Total Generation, Loading & Demand :

## Slide 23: Comparing between the cases:
Normal case ( 6.6 KV) |  |  |  | Changing swing bus (6.6-11) KV |  |  |  |  | Maximum Case |  |  | 
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V% | Bus | Initial Voltage (KV) | Operating Voltage (KV) |  | V% | Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Medium voltage |  |  |  |  |  |  |  |  |  |  |  | 
Bus100 | 6.600 | 5.9 | 89.4 | Bus100 | 11.00 | 10.245 | 93.1 |  | Bus100 | 11.00 | 11.531 | 104.8
Bus178 | 6.600 | 5.805 | 87.9 | Bus178 | 11.00 | 10.19 | 92.6 |  | Bus178 | 11.00 | 11.478 | 104.3
Bus179 | 6.600 | 5.807 | 88 | Bus179 | 11.00 | 10.191 | 92.6 |  | Bus179 | 11.00 | 11.480 | 104.4
Bus185 | 6.600 | 5.667 | 85.9 | Bus185 | 11.00 | 10.116 | 92 |  | Bus185 | 11.00 | 11.419 | 103.8
Bus223 | 6.600 | 6.04 | 91.5 | Bus223 | 11.00 | 10.325 | 93.9 |  | Bus223 | 11.00 | 11.579 | 105.3
Bus224 | 6.600 | 6.038 | 91.5 | Bus224 | 11.00 | 10.325 | 93.9 |  | Bus224 | 11.00 | 11.579 | 105.3
Low Voltage (0.4 KV) |  |  |  |  |  |  |  |  |  |  |  | 
Bus108 | 0.400 | 0.352 | 88 | Bus108 | 0.400 | 0.371 | 92.6 |  | Bus108 | 0.400 | 0.417 | 104.3
Bus110 | 0.400 | 0.352 | 88 | Bus110 | 0.400 | 0.371 | 92.6 |  | Bus110 | 0.400 | 0.417 | 104.4
Bus154 | 0.400 | 0.340 | 85.1 | Bus154 | 0.400 | 0.367 | 91.7 |  | Bus154 | 0.400 | 0.414 | 103.5
Bus156 | 0.400 | 0.340 | 84.9 | Bus156 | 0.400 | 0.367 | 97.6 |  | Bus156 | 0.400 | 0.414 | 103.5
Bus27 | 0.400 | 0.354 | 88.5 | Bus27 | 0.400 | 0.371 | 92.8 |  | Bus27 | 0.400 | 0.417 | 104.3
Bus60 | 0.400 | 0.355 | 88.8 | Bus60 | 0.400 | 0.372 | 93 |  | Bus60 | 0.400 | 0.419 | 104.7

## Slide 24
Minimum Case |  |  |  | Post- fault Case |  |  | 
Bus | Initial Voltage (KV) | Operating Voltage (KV) | V% | Bus | Initial Voltage (KV) | Operating Voltage (KV) | V%
Medium voltage |  |  |  |  |  |  | 
Bus100 | 11.00 | 11.254 | 102.3 | Bus100 | 11.00 | 11.53 | 104.8
Bus178 | 11.00 | 11.228 | 102.1 | Bus178 | 11.00 | 11.477 | 104.3
Bus179 | 11.00 | 11.229 | 102.1 | Bus179 | 11.00 | 11.479 | 104.4
Bus185 | 11.00 | 11.2 | 101.8 | Bus185 | 11.00 | 11.418 | 103.8
Bus223 | 11.00 | 11.3 | 102.7 | Bus223 | 11.00 | 11.471 | 104.3
Bus224 | 11.00 | 11.299 | 102.7 | Bus224 | 11.00 | 11.470 | 104.3
Low Voltage (0.4 KV) |  |  |  |  |  |  | 
Bus108 | 0.400 | 0.408 | 102.1 | Bus108 | 0.400 | 0.417 | 104.3
Bus110 | 0.400 | 0.408 | 102.1 | Bus110 | 0.400 | 0.417 | 104.3
Bus154 | 0.400 | 0.407 | 101.6 | Bus154 | 0.400 | 0.414 | 103.5
Bus156 | 0.400 | 0.407 | 101.7 | Bus156 | 0.400 | 0.414 | 103.5
Bus27 | 0.400 | 0.409 | 102.2 | Bus27 | 0.400 | 0.413 | 103.4
Bus60 | 0.400 | 0.410 | 102.4 | Bus60 | 0.400 | 0.419 | 104.7

## Slide 25
The following table shows the apparent
losses for these five cases::
Post –fault case | Minimum Case | Maximum Case | Changing swing bus (6.6-11)kV | Normal Case (6.6)kV | ---------------
0.362 | 0.085 | 0.334 | 0.417 | 1.020 | Real Losses ( MW)
2.116 | 0.494 | 2.081 | 2.355 | 3.196 | Reactive Losses ( MAvr)

## Slide 26
Comparison between the cases considering
the power factor:
Post –fault case | Minimum Case | Maximum Case | Changing swing bus (6.6-11)kV | Normal Case (6.6)kV | ---------------
90.70 Lag | 90.84 Lag | 90.75 Lag | 80.76 Lag | 79.97 Lag | Power Factor Swing Bus

## Slide 27
Economical Study
*Saving in penalties of PF= 79023.69 NIS/year
*Saving in losses= 305373.6 NIS/year
*Total cost of capacitor banks = (4200 * 15 ) = 63000 NIS
*Simple Payback Period= 0.18 year= 2.16 month

## Slide 28
Industrial Region of Bait- Foureek:
The industrial region suggested in bait- Foureek which will be connected to the connection point of Howara at a high voltage of 33 kV, which has an estimated load of 10 MW depending on the information given by Northern Electricity Distribution Company (NEDCO), where a transformer will be used of 33/0.4 kV. No transformer will be used to convert from 33/11 kV and that's due to economical reasons.

## Slide 29: * Since the industrial region is directly connected to the connection point of Howara, there's no need for a load flow study for the whole network which is connected to it.

## Slide 30
Calculation:
Real Power = 10 MW
Power Factor = 0.85
Using Transformer of (33-0.4) KV
Apparent Power S = ( Real Power / Power Factor)
S = ( 10 / 0.85 ) = 11.76 MVA
S Rated Transformer = ( S Load / Load Factor)
S = ( 11.76 / 0.7 ) = 16.8 MVA

## Slide 31: Conclusion:
After subjecting "Mojair Addin" network to a
load flow study and improving it, drop
voltage was clearly decreased, apparent
losses was reduced, and the power factor was
improved which will lead to a more efficient
and stable system and to economical benefits
on both NEDCO company and consumers as well.

## Slide 32
THANK YOU FOR YOUR ATTENTION