## Slide 1: The Design of Water And Wastewater Networks For Qilqis
For Hebron southern Regions Prepared by Under Supervision of Amer Mutlak Zalloum Dr.Anan Jayoussi.

## Slide 2: Outline
Objectives
Study Area
Design Methodology
Questionnaire Analysis
Water Network Design And Results
Wastewater Network Design And Results

## Slide 3: Objectives
Design a reliable water and wastewater network.
Meet the PWA design standards
Make sure that the networks performance are acceptable for the required design period.

## Slide 4: Study Area
This project provided for Qilqis village, which is locate to the south of Hebron city.

## Slide 5: Study Area
Information about Qilqis:
1- Expected population at the end of the design period=7282 person.
2-Total area=7639 dunums.
3-Density= .95 person/dunum.
4-Cunsumption/Capital=120 L/d.
5-Losses in water network=10.8%.
6-Requierd demand=135 L/c.d.
7-MaxDF=1.6 and MinDF=.45 .
8- Wastewater production=80%*Consumption/Capital=96 L/c.d.
9- Infiltration=20%*Consumption/Capital=24.
10-Harmon’s Peaking Factor=3.1.
11- sewer load/capital =96*3.1+24=321.6 L/c.d.
12- sewer load/Dunum= 306.72L/D/D.

## Slide 6: Design Methodology
Water And Wastewater Networks
Gathering Data
Modified Data
Loads Calculation/Dunum
Water And Sewer Cad
Networks Modifications
Results
AutoCAD
GIS
Drawing
Thiessen Polygon
Run

## Slide 7: Questionnaire Analysis
Chart: Availability Of water Distribution Network
| no | yes
Percent% | 33.3 | 66.7
1- Availability Of water Distribution Network

## Slide 8: Questionnaire Analysis
Chart: Main Water Source
| Tanks | Network
Percent% | 73.3 | 26.7
2-Main Water Source

## Slide 9: Questionnaire Analysis
Chart: Number Of Family Members
| 4 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 8 | 8 | 8 | 9 | 9 | 9 | 10 | 12 | 12 | 12 | 12 | 13 | 14 | 20 | 22 | 25 | 25 | 25 | 26
demand (L/c/d) | 100 | 62.5 | 71.4286 | 133.3333 | 166.6667 | 166.6667 | 83.3333 | 166.6667 | 111.1111 | 83.3333 | 60 | 111.1111 | 38.4615 | 138.8889 | 111.1111 | 148.1481 | 133.3333 | 83.3333 | 53.3333 | 53.3333 | 74.0741 | 25 | 100 | 60.6061 | 83.3333 | 25.641 | 83.3333 | 107.1429 | 83.3333 | 74.0741
3- Relation between Monthly Consumption/family and Number Of Family Members

## Slide 10: Questionnaire Analysis
Chart: Income (NIS)
| 1500 | 1500 | 2500 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3500 | 4000 | 4000 | 4000 | 4000 | 4000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 6000 | 6000 | 6000 | 6000
total demand (m cube) | 20 | 20 | 15 | 15 | 20 | 25 | 20 | 25 | 20 | 15 | 45 | 20 | 15 | 40 | 15 | 15 | 40 | 30 | 20 | 50 | 20 | 20 | 40 | 30 | 40 | 30 | 40 | 15 | 20 | 45
4- Relation between Monthly Consumption/family and Income (NIS)

## Slide 11: Water Distribution Network
WDN layout for Qilqis village.

## Slide 12: Constraints
Constraints are provided to Guarantee performance of network:
1- velocity (.01-3)m/s.
2-pressure (20-100)mH2O.

## Slide 13: Design Results
Analysis For Junctions at high demand conditions

## Slide 14
Analysis For Junctions high demand conditions

## Slide 15
Analysis For pipes at high demand conditions

## Slide 16
Analysis For pipes

## Slide 17: Results
Comments on results:
1-pressure vary from 24 to102 mH2O at low demand conditions and 17 to 98 at high demand conditions.
2- Velocity within pipes vary from .01 to .28 m/s low demand conditions and .02 to .99 m/s high demand conditions

## Slide 18: Diameters
.

## Slide 19: WDN Expected Cost

## Slide 20: Wastewater Collection Network
WCN layout for Qilqis village

## Slide 21: Constraints
Slope from .5%-15%.
Velocity from .1-3 m/s.
Cover from 1-5 m.

## Slide 22: Design Results
Slope

## Slide 23: Design Results
Velocity

## Slide 24: Design Results
Cover

## Slide 25: Profile

## Slide 26: Diameters

## Slide 27: Results
Slope vary from .5%-15%
Cover vary from 1to 5.79 m
Velocity vary from .1-2.11 m/s
Diameters 6 and 8 inch