## Slide 1: Reanalysis and Design of Bissan Air Condition Factory
- Osama Dwaikat - Osama Bsharat - Waseem Kittaneh - Salah Hanaysheh
Graduation Project 2
Wednesday 16/05/2018

## Slide 2: Contents
Introduction
Preliminary Design
3D Static Analysis and Design
3D Dynamic Analysis and Design
Concrete design
Steel design

## Slide 3: Project Description
Location
It is located at east of Tulkarm at 120 m elevation above mean sea level. It’s extended over an area 2900 m2
Stories and usage

## Slide 5: Codes and Standards
American Concrete Institute (ACI 318-14).
American Society of Civil Engineers (ASCE 7-10).
American Institute of Steel Construction (AISC 360-16).
International Building Code (IBC -2012).
American Society for Testing and Materials (ASTM A615M).

## Slide 6: Materials
Reinforcement Concrete
Rebar Steel
Structural Steel
Roof Sheeting
Glass
Cable
Bolts
Weld

## Slide 7: Loads Types
Dead Load
Superimposed dead load
Live Load
Snow Load
Soil pressure
Wind Load
Earthquake load

## Slide 8: SD Load
In our structure, it is about these elements:
SD on concrete Slabs (tiles, partitions, false ceiling,…etc)
Masonry Wall
Steel Roof (solar panels, lighting and HVAC system)
Minaret

## Slide 9: Wind Load
Z (qz) = 0.0613 * Kz * Kzt * Kd * V2 *I
Kd: Directionality factor. Kzt: Topographic factor. Kz: Pressure-exposure coefficient depends on roughness, exposure and the height. I: Importance factor depends on occupancy type. v: basic wind speed (m/sec)

## Slide 10: Wind Load
Kd = 0.85 Kzt = 1 v = 130 km/hr = 36.11 m/sec I = 1 (Occupancy type I) Kz= 1.27 (Roughness C and Exposure D)
P design = P ext - P int
Pint or ext = qz* G * Cp
G: Gust factor.
Cp: pressure coefficient.

## Slide 11: Loads values
Superimposed dead load
Office slab = 4.77 kN/m2
Ground slab = 3.27 kN/m2
Masonry Wall loads = 17.5 kN/m
Steel roof = 0.6 kN/m2
Minaret glass wall = 0.64 kN/m2
Live load
Office slab = 2.5 kN/m2
Ground slab = 6 kN/m2
Steel roof = 1 kN/m2
Minaret = 3 kN/m2
Snow load
Steel roof = 0.6 kN/m2
Wind load
Walls = 0.77 kN/m2
Roof = 0.80 and 0.77 kN/m2
Soil Pressure
q = 19 kN/m

## Slide 12: Combinations
Strength Combinations
Service Combinations

## Slide 13: Preliminary Design
Slabs
Office
Ground
Basement
Columns
Office
Ground
Basement
Beams
Office
Ground
Shear Wall

## Slide 14: Office Beams and Slab
Assumptions
Columns Dimensions (40*25 cm)
αfm < 2
Beams dimensions
 h = 0.16 m

## Slide 15: Ground Beams and Slab
Assumptions
Columns Dimensions (40*25 cm)
αfm < 2
Beams dimensions
 h = 0.20 m

## Slide 16: Basement Slab
Blind slab:
h = 0.15 m
It used to cover the backfill

## Slide 17: Columns
Ground columns
Assume ρ = 1%
Based on calculations:  180 x 180 mm
But the used dimension is:
 250 x 400 mm
Basement columns
Assume ρ = 1%
Based on calculations:  275 x 275 mm
But the used dimension is:
 250 x 400 mm

## Slide 18: Shear Wall
Assumptions:
γ soil = 18 kN/m3
Øsoil = 30˚
Wall Thickness is 25 cm
Vu = 48.34 kN
ØVc = 119 kN

## Slide 19: 3D Static Analysis and Design
Modeling in SAP2000
Analysis Verifications
Deflection
Results

## Slide 20: Modeling in SAP2000

## Slide 21: Analysis Verifications
Compatibility check
Deflection
Equilibrium check
Internal Forces
Dead Load
Superimposed Dead Load
Live Load
Snow Load
Lateral Load

## Slide 22: Compatibility check
From the figure, it is clear that the component of the structure looks compatible with each other.

## Slide 23: Deflection Computations
Concrete deflection:
Allowable deflection  ∆LT = = = 0.0229 m
To measure long term deflection, define a combination (2DL+1.5LL)
From SAP  0.0224 m (OK)

## Slide 24: Deflection Computations
Steel deflection limit:
Live load deflection =
Snow and wind load deflection =
Dead + Live deflection =

## Slide 25: Deflection Computations
Live load deflection :
Δallowable = 158 mm.
From SAP  Δ = 90 mm (OK)
Snow and wind load deflection :
Δallowable = 158 mm.
From SAP  Δsnow = 54.30 mm (OK)
Δwind = 22.80 mm (OK)
(Dead + Live) deflection :
Δallowable = 237 mm.
From SAP  Δ = 194.50 mm (OK)

## Slide 26: Gravity Loads (Dead)
For Concrete:
Total DL = W(slabs) +W(beams) + W(columns) + W(shear walls) = 19867.5 kN.
From SAP  Dead Load = 19874.5 kN
Difference % = % = = 0.035 % (OK)

## Slide 27: Gravity Loads (SD)
Total SD = SD office + SD ground + SD roof + SD walls (concrete +glass)
= 8854.7 kN
From SAP  SD = 8863.7 kN
Difference % = = 0.1 % (OK)

## Slide 28: Gravity Loads (Live)
Total LL = LL office + LL ground + LL roof + LL minaret = 10171kN
From SAP  LL = 10182.7 kN
Difference % = % = 0.11 % (OK)

## Slide 29: Gravity Loads (Snow)
Total SL = 1586.8 kN
From SAP  Snow Load = 1590.7 kN
Difference % = % = 0.25 % (OK)

## Slide 30: Lateral Load
Total lateral load in X – direction = 688.7 kN
From SAP  Lateral Load in X – direction = 683.59 kN
Difference % = *100% = 0.74 % (OK)

## Slide 31: Lateral Load
Total lateral load in Y – direction = 404 kN
From SAP  Lateral Load in Y – direction = 411.7 kN
Difference % = *100% = 1.92 % (OK)

## Slide 32: Internal forces
Moment check:
Moment in Y – direction
Total static Moment =610.4 kN.m
From SAP  TSM = 556 kN.m
Difference %= *100% = 8.9 % (OK)
Moment in X – direction
Total static Moment =828.2 kN.m
From SAP  TSM = 788.5 kN.m
Difference %=*100% = 4.79 % (OK)

## Slide 33: Internal forces
Shear check:
Vu = 85.48 kN
From SAP  Vu = 82.23 kN
Difference % = * 100% = 3.8 % (OK)

## Slide 34: Results
Steel sections | 
static design | 
Columns | Tube 140*140*12.5
 | H400*237
 | H400*314
 | H400*422
Ring beam | 120*120*12.5
Rafters | HE400M
 | HE280M
Girder | HE400M
Purlins | 120*84*7.1
Bracing | 100*100*10
Cables | Diameter = 22 mm
Concrete sections | 
static design | 
Columns | 
Group A | 0.60 x 0.25
Group B | 0.55 x 0.50
Group C | 0.80 x 0.45
Beams | 
Ground | 0.60 x 0.40
Office | 0.60 x 0.40
Tie | 0.60 x 0.30
Slabs | 
All | 0.25
Wall | 
All | 0.25

## Slide 35: 3D Dynamic Analysis and Design
Mass source definition
Irregularity check
Mass participation ratio
Period check
Seismic analysis
Seismic checks
Results

## Slide 36: Mass source definition
All SD load and 35% of live load considered as permanent mass.

## Slide 37: Irregularity check
Block A
Block B

## Slide 38: Mass participation ratio
Ritz vectors method was used to determine the most expected modes of the modal analysis of structure.

## Slide 39: Period check
 | Approximation | Rayleigh | SAP
Block A | 0.61 | 0.577 | 0.586
Block B | 0.64 | 0.74 | 0.7

## Slide 40: Seismic analysis
Seismic parameters
Equivalent static definition
Response spectrum definition

## Slide 41: Seismic parameters
Site classification “C”
Seismic importance factor I = 1
Response modification factor R = 4.5
Seismic zone factor Z = 0.15
Based on Ss = 0.375, S1 = 0.1875
Fa = 1.2
Fv = 1.6125
SDS = 0.3
SD1 = 0.2
Seismic design category “D”

## Slide 42: Equivalent static definition
According to IBC-2012

## Slide 43: Response spectrum definition

## Slide 44: Seismic checks
Base shear
 | V (kN) | Vmin (kN) | Vmax (kN) | VSAP (kN)
Block A | 146 | 28.35 | 162 | 137
Block B | 2181 | 423.2 | 2050 | 2006

## Slide 45: Seismic checks
Drift check
Block A
Block B

## Slide 46: Results
Steel sections | 
dynamic design | 
Columns | Tube 140*140*12.5
 | H400*237
 | H400*314
 | H400*509
Ring beam | 120*120*12.5
Rafters | HE400M
 | HE280M
Girder | HE400M
Purlins | 120*84*7.1
Bracing | 120*84*12.5
Cables | Diameter = 22 mm
Concrete sections | 
dynamic design | 
Columns | 
Group A | 0.60 x 0.25
Group B | 0.55 x 0.50
Group C | 0.80 x 0.45
Group D | 0.40 x 0.40
Beams | 
Ground | 0.60 x 0.40
Office | 0.60 x 0.40
Tie | 0.60 x 0.30
Slabs | 
All | 0.25
Wall | 
All | 0.25

## Slide 47: Concrete design
Slabs
Beams
Columns
Shear walls
Footings

## Slide 48: Slabs
Ground slab
Max moment = 28.8 kN.m/m
As = 450 mm2/m.  Use 4Ø12/m.
Office slab
Max moment = 27.4 kN.m/m
As= 450 mm2/m  Use 4Ø12/m.
Blinding slab (15 cm)
As = 270 mm2/m Use 4Ø10/m.

## Slide 49: Beams
Simply supported

## Slide 50: Beams
One-end continuous

## Slide 51: Beams
Two-end continuous

## Slide 52: Columns

## Slide 55: Shear walls
Vertical rebar
In side of soil: Mmax = 72 kN.m/m, As = 825 mm2/m  Use 5Ø16/m
In other side: As = = = 375 mm2/m  Use 4Ø12/m
Horizontal rebar
As = = = 375 mm2/m  Use 4Ø12/m in each side.

## Slide 56: Footings
Footing | Column | Load Limit (KN) | Footing Dimension (m) |  |  | Area Of Bottom Reinforcement (mm^2) |  | 
Name | Dimension (m) | Service Load | Length | Width | Depth | As, Cal. | Minimum | No. of Bars
F1 | 0.6*0.25 | Less than 500 | 1.6 | 1.25 | 0.35 | 387.1 | 630 | 5Ø14/m
F2 |  | 500-750 | 1.95 | 1.6 | 0.35 | 722.8 | 630 | 5Ø14/m
F3 | 0.4*0.4 | --- | 1 | 1 | 0.35 | 95.7 | 630 | 5Ø14/m
F4 | 0.8*0.45 | --- | 2.4 | 2.05 | 0.35 | 997.8 | 630 | 5Ø16/m
F5 | 0.55*0.5 | Less than 500 | 1.25 | 1.25 | 0.35 | 186.8 | 630 | 5Ø14/m
F6 |  | 500-850 | 1.85 | 1.85 | 0.35 | 645.6 | 630 | 5Ø14/m
F7 | Combined Column | --- | 2.4 | 1.9 | 0.35 | 697.0 | 630 | 5Ø14/m
F8 | Combined footing | --- | 3 | 2.1 | 0.35 | 963.0 | 630 | 5Ø16/m
Wall | Wall footing | --- | --- | 1.2 | 0.35 | 98.7 | 630 | 5Ø14/m

## Slide 57: Steel member design
Tension Capacity
Compression Capacity
Buckling
Moment Capacity
Lateral Torsional Buckling
Shear Capacity
Beam-Column Capacity

## Slide 58: Tension Capacity
ØTn = Ø * Fy * Ag
ØTn: Tension capacity for the member.
Ø: Reduction factor. In tension Ø = 0.9
Fy: Yielding stress of steel.
Ag: Gross sectional area of the member.
Group | Sections Name | SAP | 
 |  | ØTn(kN) | Tu(kN)
Columns | TUBO 140*140*12.5 | 1424.112 | 0
 | H400*314 | 8935.6 | 0
 | H400*237 | 6746.4 | 0
 | H400*509 | 14475.6 | 0
Rafter | HE400M | 7282.5 | 0
 | HE280M | 5361.4 | 0
Ring Beam | TUBO120*120*12.5 | 1207 | 65.7
Girder | HE400M | 7282.5 | 0
Purlins | TUBO120*84*7.1 | 602 | 0
Bracing | TUBO120*84*12.5 | 999.7 | 133.45
Cable | Dia. 22 mm | 285 | 274

## Slide 59: Compression Capacity
Buckling
Ø Pn = Ø * Fcr * Ag
Ø Pn: Compression capacity for the member.
Ø : Reduction factor, In compression Ø = 0.9
Fcr: Critical stress on the member.
Ag: Gross area of the member.

## Slide 60: Buckling
To find slenderness for critical column =
The lower part of column will be treated one time as concrete and another as steel to determine which case is more conservative.

## Slide 61
The buckling force in general = , but is the same in both, so, we will check the value of (EI) only.
Concrete
(EI)st < (EI)c
E= 200,000,000 kN/
I = 0.0007971
(EI)st = 200,000,000 * 0.007971
= 159,420 kN.
Steel
E= 24,870,000 kN/
I = 0.009632
(EI)c = 24,870,000 * 0.009632
= 172,399 kN.

## Slide 62: Buckling
In X-Z plan: λx = = = 26.84
In Y-Z plan:
Maximum of:
= = 20.314
= = 40.82
Since λy > λx Use λ = 40.82
λy = 40.82

## Slide 63: Buckling
λcr = = = 113.20
λcr > λ  ØFcr = Ø * * Fy
Fe = = = 1184.6 MPa.
ØFcr = 0.9 * * 250 = 206 MPa.
ØPn = ØFcr * Ag = 206*30200 = 6221.2 kN
From SAP:
ØPn = 6179.5 kN.
Maximum load = 192.5 kN.
6221.2 kN > 192.5 kN  Ok

## Slide 64
Group | Sections Name | SAP | 
 |  | ØPn(kN) | Pu(kN)
Columns | TUBO 140*140*12.5 | 935 | 202.7
 | H400*314 | 8204.8 | 275
 | H400*237 | 6179.5 | 192.5
 | H400*509 | 13382.3 | 359.8
Rafter | HE400M | 6826.3 | 417.2
 | HE280M | 3549.8 | 173.6
Ring Beam | TUBO120*120*12.5 | 1185.3 | 0
Girder | HE400M | 5557 | 30.7
Purlins | TUBO120*84*7.1 | 138 | 0
Bracing | TUBO120*84*12.5 | 150 | 111.7

## Slide 65: Moment capacity
Bending moment capacity ØMn = ØMp  If no lateral torsional buckling
ØMp, = Ø * Z * Fy
Ø : Reduction factor in moment = 0.9
Z: Plastic section modulus.

## Slide 66: Moment capacity
Rafter:
Lp = 1.76*ry* = 3.83 m
Lb= 7.2 m > 3.83 m
Lr = 11.36 m.
So, Lp < Lb < Lr
 Elasto-Plastic L.T.B
Lateral Torsional Buckling

## Slide 67: Moment capacity
Rafter:
Mp = Fy * Zx = = 1401 kN.m
My = Fy * Sx = = 1205 kN.m
ØMn= < ØMp
Cb = < 3
Cb = 1.04
ØMn = 1077.8 < ØMp = 1260.9
 ØMn = 1077.8 kN.m
Lateral Torsional Buckling

## Slide 68
Group | Sections Name | SAP | 
 |  | ØMn(kN) | Mu(kN)
Columns | TUBO 140*140*12.5 | 68.3 | 49.5
 | H400*314 | 1433.5 | 1036
 | H400*237 | 1055.9 | 547.6
 | H400*509 | 1236.9 | 839.6
Rafter | HE400M | 1244.5 | 618.3
 | HE280M | 662.6 | 319
Ring Beam | TUBO120*120*12.5 | 48.36 | 31.4
Girder | HE400M | 432 | 157
Purlins | TUBO120*84*7.1 | 24 | 14.5
Bracing | TUBO120*84*12.5 | 37.8 | 2

## Slide 69: Beam-Column Capacity
To check capacity, use interaction diagram which consist from these equations
+ < 1 , if ≤ 0.2
+ <1 , if ≥ 0.2

## Slide 70
Group | Sections Name | ØPn(kN) | Pu(kN) | Pu/ØPn | ØMn(kN) | Mu(kN) | Beam – Column capacity | Result
Columns | TUBO 140*140*12.5 | 935 | 202.7 | 0.217 | 68.3 | 49.5 | 0.86 | Ok
 | H400*314 | 8204.8 | 275 | 0.034 | 1433.5 | 1036 | 0.74 | Ok
 | H400*237 | 6179.5 | 192.5 | 0.031 | 1055.9 | 547.6 | 0.53 | Ok
 | H400*509 | 13382.3 | 359.8 | 0.027 | 1236.9 | 839.6 | 0.69 | Ok
Rafter | HE400M | 6826.3 | 417.2 | 0.061 | 1244.5 | 618.3 | 0.53 | Ok
 | HE280M | 3549.8 | 173.6 | 0.049 | 662.6 | 319 | 0.51 | Ok
Ring Beam | TUBO120*120*12.5 | 1185.3 | 0 | 0.000 | 48.36 | 31.4 | 0.65 | Ok
Girder | HE400M | 5557 | 30.7 | 0.006 | 432 | 157 | 0.37 | Ok

## Slide 71: Shear capacity
Shear buckling:
≤ 2.24 *
If No shear buckling  Check it for shear yielding (calculate its shear capacity)
Shear Yielding:
ØVn = Ø * 0.6 * Fy * Aweb
Ø: Reduction factor, in shear = 1
Aweb: Gross sectional area of the member, which is parallel to shear force.

## Slide 72
Group | Sections Name | SAP | 
 |  | ØVn(kN) | Vu(kN)
Columns | TUBO 140*140*12.5 | 343.5 | 20.16
 | H400*314 | 1459.5 | 195.38
 | H400*237 | 1049.7 | 144.8
 | H400*509 | 2617.7 | 44.5
Rafter | HE400M | 1351 | 163.8
 | HE280M | 854 | 124
Ring Beam | TUBO120*120*12.5 | 276.45 | 44.6
Girder | HE400M | 1351 | 97.6
Purlins | TUBO120*84*7.1 | 188 | 3
Bracing | TUBO120*84*12.5 | 276.4 | 0

## Slide 73: Steel Connections Design
Steel Connections Design

## Slide 74: Steel Connections Design
n | Connection Type |  |  |  | 
1 | Bracing | Column | 6 | Rafter | Tube Column
 | Tube 120x84x12.5 | H400x314 |  | HE 400M | Tube 140x140x12.5
2 | Purlins | Rafter | 7 | Girder | Column - flange
 | Tube 120x84x7.1 | HE 400M |  | HE 400M | H 400x314
3 | Cable | Rafter | 8 | Girder | Column - top
 | 22 mm diameter | HE 400M |  | HE 400M | H 400x509
4 | Rafter | Column | 9 | Rafter | Rafter
 | HE 400M | H 400x314 |  | HE 400M | HE 400M
5 | Rafter | Column | 10 | Rafter | Rafter
 | HE 280M | H400x237 |  | HE 280M | HE 280M
18 | Rafter | Column | 11 | Rafter | Girder
 | HE 280M | H400x237 |  | HE 400M | HE 400M

## Slide 75: Cable connection
By assuming 15 mm thickness:
Weld fracture check Rn < ∅ (ƩL) (a cos 45) (0.6 FEXX)  a = 8 mm
Tear-out check Rn < ∅ (0.6 Fu)*2*Lc*tp  Lc, min = 51 mm
Bearing check Rn < ∅*C*Fu*db*tp = 274*103 < 343*103  Ok

## Slide 76: Base plate connection
Base plate |  | 
12 | Tube 140x140x12.5 | on column 60x25
13 | Tube 140x140x12.5 | on slab
14 | H 400x509 | on slab
15 | H 400x314 | on column 55x50
 |  | and column 45x80
16 | H 400x237 | on column 55x50
17 | Tube 120x120x12.5 | Ring beam

## Slide 77: Base plate connection
Tension check  db = 17.86 mm
Shear check  db = 13.11 mm For top bolts  Use db = ⅞”
Shear-tension interaction + ≤ 1.3 = 0.99 < 1.3 (Ok)
Bearing check
Rn ≤ Ø*C*Fu*db*tp 47.5 kN < 160 kN  Ok
Notes: Tear-out check:
Since edge distance = 35.56 mm > 2 (15.875) = 31.75 mm
No tear-out failure.

## Slide 78
Assume ’’ diameter.
Tension check 69.7 kN < 112.54 kN
Shear check 105.5 kN < 162.6 kN
Shear-tension interaction + ≤ 1.3 = 1.268 < 1.3 (Ok)
Bearing check 18 kN < 343 kN  Ok
Base plate connection
Notes: Tear-out check:
Since edge distance = 35.56 mm > 2 (15.875) = 31.75 mm
No tear-out failure.

## Slide 79: Base plate connection
Yielding failure:
Myield = Fy * Sx = 245 * = = 4.6 kN.m
T @one side in flange = + = + = 615.5 kN
M’ = 615.5 * 0.03 = 18.47 kN.m
Mstiffener =18.47 – 4.6 = 13.87 kN.m
Astiffener = = 699 mm2
t = = 10 mm

## Slide 80: At the END ..

## Slide 81: THANK YOU