## Slide 1: Design a Water and Wastewater Network for Qabatiya Town
Prepared By :
Mustafa Ali Mohammad Alawneh
Supervisor :
Dr. Anan Jayousi

## Slide 2: Content: -
Objectives.
Overview of Qabatiya.
The Questionnaire.
Modeling & Analyzing the Existing Network.
Design a Future Water Network.
Design a Wastewater Network.

## Slide 3: Objectives: -
Analyze the Existing Water Distribution Network to find out the problems and suggest a solutions to solve these problems.
Design a Future Water Network to overcome the problems in the old network and to be able to meet the future water demand for the next 20 years.
Design a Wastewater Network for the town to serve the town for the next 20 years.

## Slide 4: Overview of Qabatiya: -
Location:
Located in the middle of the Jenin governorate, with total area 50.747 Km2.
Population:
The total population of the town was 24,439 capita in 2017.

## Slide 5
Overview of Qabatiya: -
Topography:
The town elevation vary from 250 m to 450 m above the mean sea level.
Land Use:
The town famous with agriculture and quarries.

## Slide 6: The Questionnaire

## Slide 7: The Questionnaire: -
Chart: source of Water
| Water Tank | Municipality | Municipality + Gathering Well + Water Tank | Municipality + Gathering Well | Gathering Wall
 | 2 | 28 | 7 | 2 | 1

## Slide 8: The Questionnaire: -
Chart: FREQUENT DURING WEEK
| 1 | 2 | 3 | 4 | 5 | 6 | 7
 | 3 | 6 | 9 | 1 | 7 | 0 | 14

## Slide 9: The Questionnaire: -
Chart: Pressure
| High | Low | Moderate
 | 24 | 5 | 11

## Slide 10: The Questionnaire: -

## Slide 11: The Questionnaire: -
Chart: CONSUMPTION VARIARTION
| 2 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9

 | 33.3333 | 166.6667 | 55.5556 | 111.1111 | 44.4444 | 83.3333 | 33.3333 | 41.6667 | 41.6667 | 33.3333 | 66.6667 | 125 | 80 | 53.3333 | 106.6667 | 16.6667 | 55.5556 | 33.3333 | 133.3333 | 66.6667 | 16.6667 | 33.3333 | 111.1111 | 38.8889 | 95.2381 | 23.8095 | 28.5714 | 61.9048 | 80.9524 | 33.3333 | 80.9524 | 38.0952 | 51.8519

## Slide 12: The Existing Water Network

## Slide 13: The Network: -
2 Tanks. (1500m3 & 500m3).
285 Nodes.
301 Pipes. (1,2,3,4,6) inch.
70 Km total length.

## Slide 14: The Network: -
Obtained the network by using the ModelBuilder.
Using Thiessen Polygon Creator to divide the entire served area.

## Slide 15: The Network: -
Demand and Supply Calculation :
Estimate the amount of water needed by citizens.
Total population = 24,439 capita.
The consumption rate = 56 L/c-day.
The losses rate = 48.72%.
.

## Slide 16: The Network: -
Used Demand Pattern.

## Slide 17: Results: -
Chart: Junction Number
Chart: Junction Number
Pressure at 2:00 pm.
Pressure at 4:00 am.
When Tank-1 Works :

## Slide 18: Results: -
Chart: Pipe Number
Chart: Pipe Number
Velocity at 2:00 pm.
Velocity at 4:00 am.

## Slide 19: Results: -
Chart: Junction Number
When Tank-2 take a place.
Pressure at 10:00 pm.

## Slide 20: The Designed Water Network

## Slide 21: The Designed Network: -
General Conditions:
24 hrs. Supply.
Separate the Network.
Design period 20 years.
Modify the old & the small pipes.
Used the same Demand Pattern.

## Slide 22
Calculations:
Population projection:
Pt= P0 ×.
P0 )2007) = 18,968 capita.
Pt (2017) = 24,439 capita.
t1 = 10 years.
K = 2.53%.
t2 = 20 years.
So, Pt(2037) = 24,439 × = 40,571 capita.
The Designed Network: -

## Slide 23
Future Per Capita Consumption:
Water Consumption per capita = 120 L/day, according to PWA.
Physical Losses rate = 15%.
Total Future consumption (demand) = .
Total Future consumption (demand) =
Total Future Supply =
Peak Factor = .
Peak Factor = = 3.56 .
The Designed Network: -

## Slide 24
The Designed Network: -
Results:
Pressure at 2:00 pm.
Pressure at 4:00 am.
Chart: Junction Number
Chart: Junction Number

## Slide 25
Used a PRV:
The Designed Network: -
PRV Properties

## Slide 26
The Designed Network: -
Results after used a PRV:
Pressure at 2:00 pm.
Pressure at 4:00 am.
Chart: Junction Number
Chart: Junction Number

## Slide 27
The Designed Network: -
Results:
Velocity at 2:00 pm.
Velocity at 4:00 am.
Chart: Pipe Number
Chart: Pipe Number

## Slide 28
The Designed Network: -
Final Modified Network.

## Slide 29
The Designed Network: -
Results:
Length of Modified Pipes:
Diameter (in) | Length (m)
1 | 1789
2 | 7565
3 | 4902
4 | 13028
6 | 6879
8 | 163
10 | 1404
12 | 775

## Slide 30
The Designed Network: -
Storage Facilities:
The capacity of the reservoir needed is = m3.
So, by considering an hourly peak factor (1.4), tank capacity needed is equal 1000 m3.
The existing storage capacity of 1500 m3 is sufficient.

## Slide 31
24 Hours/Day | Demand pattern | Cumulative demand pattern | Difference between 24hours and cumulative
1 | 0.7 | 0.7 | -0.3
2 | 0.6 | 1.3 | -0.7
3 | 0.4 | 1.7 | -1.3
4 | 0.4 | 2.1 | -1.9
5 | 0.6 | 2.7 | -2.3
6 | 0.9 | 3.6 | -2.4
7 | 1 | 4.6 | -2.4
8 | 1.2 | 5.8 | -2.2
9 | 1.2 | 7 | -2
10 | 1.2 | 8.2 | -1.8
11 | 1.2 | 9.4 | -1.6
12 | 1.1 | 10.5 | -1.5
13 | 1.1 | 11.6 | -1.4
14 | 1.4 | 13 | -1
15 | 1.4 | 14.4 | -0.6
16 | 1.4 | 15.8 | -0.2
17 | 1.4 | 17.2 | 0.2
18 | 1.2 | 18.4 | 0.4
19 | 1.2 | 19.6 | 0.6
20 | 1.1 | 20.7 | 0.7
21 | 1 | 21.7 | 0.7
22 | 0.8 | 22.5 | 0.5
23 | 0.8 | 23.3 | 0.3
24 | 0.7 | 24 | 0

## Slide 32
The Designed Network: -
Cost Estimate:
Diameter (in) | Length (m) | Tax | Transmission | Trench Excavation | Trench Excavation | Trench backfilling | Trench backfilling | Installation and fittings | Unit price /m |  | Total price (NIS)
1 | 1789 | 1 | 28 | 22 | 22 | 30 | 30 | 15 | 95 |  | 169,955
2 | 7565 | 1 | 30 | 25 | 25 | 40 | 40 | 20 | 115 |  | 869,975
3 | 4902 | 1 | 35 | 28 | 28 | 42 | 42 | 25 | 130 |  | 637,260
4 | 13028 | 1 | 67 | 50 | 50 | 64 | 64 | 30 | 211 |  | 2,748,908
6 | 6879 | 1 | 105 | 60 | 60 | 74 | 74 | 35 | 274 |  | 1,884,846
8 | 163 | 1 | 145 | 70 | 70 | 75 | 75 | 40 | 330 |  | 53,790
10 | 1404 | 1 | 200 | 80 | 80 | 80 | 80 | 45 | 405 |  | 56,8620
12 | 775 | 1 | 300 | 150 | 150 | 160 | 160 | 90 | 700 |  | 542,500
Item |  |  | Unit |  | Quantity |  | Unit price |  |  | Total price | 
The Pressure Reduce Valve |  |  | Item |  | 1 |  | 50,000 |  |  | 50,000 | 
Total Price |  |  |  |  |  |  |  |  |  | 7,525,854 | 

## Slide 33: The Designed Wastewater Network

## Slide 34
Wastewater Network: -
The town doesn’t have a Wastewater Network.
People depend on the suction to dispose the wastes.
The terrain of the town allows to use gravity flow concept.
Part of a sewage network designed, to represent the concept of gravity flow.

## Slide 35
Location of the Outfall, and the recommended Treatment Plant.
Wastewater Network: -
Location of the Outfall, and the recommended Treatment Plant.

## Slide 36
Assumption and Constrains for the Design:
Design period 20 years.
Future Population = 40,571 capita.
120 L/C-D. water demand.
80% of produced waste water from consumed water.
20% infiltration.
Peak factor calculated by (PF =14P-1/6).
The maximum distance between manholes is 30m.
PVC circular pipes.
Velocity constrains between (0.6 – 3) m/s.
Cover constrains between (1 – 3.5) m.
Slope constrains between (1 – 12) %.
Wastewater Network: -

## Slide 37
Wastewater Network: -
The designed part of the sewage network.

## Slide 38
Wastewater Network: -
Calculations:
The Peak Factor: PF =
Total wastewater flow m3/d.
Total flow for the town 10087.6 m3/day
The rate of flow covered by the designed network: .
The flow occupied by the deigned network = = 5003.45 m3/day.
Load on each manhole = m3/day.
The load of second part of the town, loaded in manhole (MH-342) = 10087.6 – 5003.45 = 5084.15 m3/day.

## Slide 39
Wastewater Network: -
Results:
Slope.
Chart: Conduit Number

## Slide 40
Wastewater Network: -
Results:
Velocity.
Chart: Conduit Number

## Slide 41
Wastewater Network: -
Results:
Covers:
Maximum cover.

## Slide 42
Wastewater Network: -
Results:
Covers:
Drop Manholes.

## Slide 43
Wastewater Network: -
Results:
Covers:
Difficult Terrain.

## Slide 44
Wastewater Network: -
Results:
Diameters.
Chart: Used Diameter
| 15 | 12 | 10 | 8
15 12 10 8 | 9.771 | 2.2901 | 1.8321 | 86.1069