## Slide 1: "Mechanical Systems For the palestinian ECONOMIC POLICY RESEARCH INSTITUTE"
Supervisor :
Eng. Ramez Al Khaldi
Prepared by :
Bahaa Yousef Malhis
Nodar Hisham Sabbah
Ameer Ghazi Malhis
Ala’a Abd An-Naser Diab

## Slide 2: Presentation out line:
- Building Description.
- Heating load calculation.
- Cooling load calculation.
- Duct Design.
- Plumbing System.
- Fire Fighting System.
- Equipment Selection.

## Slide 3: Building Description
Building Location :
Country: Palestine.
City: Ramallah
Elevation: 840 m above sea level Latitude: 32˚.
Building face sits at the south orientation.
The wind speed in Ramallah is above 5 m/s.
Building Details :
The Palestinian Economic Policy research institute consists of 6 floors, 5 up ground, one below ground.

## Slide 4: Overall Heat Transfer Coefficient, U overall
The U overall is given by:
In our project the method was used as following:
Where:
U: The overall heat transfer coefficient [W/ m².˚C].
Ri: Inside film temperature [m².˚C/W].
Ro: Outside film temperature [m².˚C/W].
K1, 2, …, n : Thermal conductivity of the material [W/m.˚C].
X1, 2, …, n : Thickness of each element of the wall construction [m].

## Slide 5: Results of overall heat transfer coefficient for each element
Type | Overall Heat Transfer Coefficient U(W/m2.K)
Outside wall | 0.74
Inside wall | 2.6
Ceiling | 0.88
Floor | 0.88
Glass | 3.5
Wood door | 3.5

## Slide 6: Heat Load Calculations
Heat loss by conduction and convection heat transfer through any surface is given by:
Where:
Q = heat transfer through walls, roof, glass, etc.
A = surface area.
U = overall heat transfer coefficient.
ΔT = Difference in outside temperature and inside temperature.
Select inside & outside design condition (from Palestinian code) :
Parameters | Winter | Parameters | Winter
Tin | 22 | Win | 8.3
Tout | 4.7 | Wout | 4.1
Φin | 50% | Tun | 30.65
Φout | 62% |  | 

## Slide 7: General Procedures for Calculating Total Heat Load:
Select inside design condition (Temperature, relative humidity).
Select outside design condition (Temperature, relative humidity).
Select unconditioned temperature (Tun).
Find over all heat transfer coefficient Uo for wall, ceiling, floor, door, windows, below grade.
Find area of wall, ceiling, floor, door, windows, below grade.
Find Qs conduction.
Find Vinf, V vent.
Find Qs, QL vent, inf.
Find Q total and Q boiler.

## Slide 8: Equations and Results for heating load calculations :
Heating load summary :
Floor | Q Total(KW)
Ground Floor | 83.8
First Floor | 48.1
Second Floor | 13.385
Third Floor | 32.74
Roof | 15.942

## Slide 9: Cooling Load Calculations :
Select inside & outside design condition (from Palestinian code) :
Parameters | summer | Parameters | summer
Tin | 22 | Win | 9.6
Tout | 30 | Wout | 16.1
Φin | 50% | Tun | 27.3
Φout | 57% |  | 

## Slide 10
In calculations of cooling load, orientation is an important basic factor during calculation, the general equation in cooling calculations is:
For transmitted through glass:
For convection through glass:

## Slide 11: Cooling Load Results:
Floor | Qtotal(KW) | Qtotal(TON)
Ground floor | 89.3 | 25.5
First floor | 47.7 | 13.6
Second floor | 45.9 | 13.1
Third floor | 47.4 | 13.5
Roof floor | 35.9 | 10.25

## Slide 12: Duct Design :
Design procedures
Number of grills and diffusers are calculated and distributed uniformly.
The total sensible heat of floor is calculated.
The Vcirculation of floor is calculated.
The main branch duct velocity is 5 m/s.
The pressure drop (∆P/L) method is achieved for duct design (by using ∆P/L(0.6 Pa/m)).
The main diameter is calculated ,at the same (∆P/L).
The height and width of the rectangular ducts are determined from software program .

## Slide 13: Equations For Design duct :
The equal pressure drop method for sizing in second floor room (12,13,14) :
FCU (No.) | section | Vcirc (l/s) | Velocity(m/s) | ∆P/L (Pa/m) | H (cm) | W (cm)
4 | AB | 424.95 | 5 | 0.6 | 30 | 37.5
 | BC | 271.25 | 3.6 | 0.6 | 30 | 25
 | CD | 174 | 3.6 | 0.6 | 30 | 200

## Slide 15: Plumbing System: Potable water:
Find number of unit for fixtures from tables , the results as shown in table:
Floor | Hot F.U | Cold F.U | Hot size(in) | Cold size(in)
Basment | 3.75 | 6.75 | 1 | 1.25
Ground floor | 10 | 40 | 1.25 | 1.5
First floor | 7.5 | 22.5 | 1.25 | 1.5
Second floor | 7.5 | 22.5 | 1.25 | 1.5
Third Floor | 7.5 | 22.5 | 1.25 | 1.5
Roof | 12.75 | 23.75 | 1.25 | 1.5
Sum | 49 | 138 | 2 | 2.5

## Slide 16: Potable water piping inside floor
For example 2nd floor:

## Slide 18: Riser: cold water:
Size(in)A | Demand (l/s) | Fixture | Section
2.5 | 3.24 | 138 | a-b
2.5 | 2.91 | 114.25 | b-c
2 | 2.57 | 91.75 | c-d
2 | 2.148 | 69.25 | d-e
1.5 | 1.45 | 46.75 | e-f
1.25 | 1.052 | 6.75 | f-6

## Slide 19: Hot water:
Size(in) | Demand(l/s) | Fixture | Section
2 | 1.81 | 49 | a-b
2 | 1.78 | 45.25 | b-c
1.5 | 1.58 | 35.25 | c-d
1.5 | 1.4 | 27.75 | d-e
1.5 | 1.25 | 20.25 | e-f
1.25 | 1.034 | 12.75 | f-6

## Slide 21: Drainage System:
Two separated stacks one for soil and the other for waste. Each stack 4 in.
(standard 4 in for WC,2 in for other fixtuers,4 in floor drain).

## Slide 23: Fire Fighting System
We used in fire system class 3 as standpipe system (cabinet and landing valves).
Class III Systems: A Class III standpipe system shall provide 11⁄2 in. (40 mm) hose stations to supply water for use by trained personnel and 21⁄2 in. (65 mm) hose connections to supply a larger volume of water for use by fire departments and those trained in handling heavy fire streams.
One riser so 500 GPM for 40 min operating the tank size = 80m^3.
Pressure for cabinet = 65 Psi and 100 Psi for landing valve.

## Slide 25: Equepments Selction
Boiler:
The heating load for building is 193.9 Kw, and load for boiler selected =1.1*193.9=213.3 Kw, since we have one boiler, Because that we choose from mansour catalog of steam boiler is MS-10 which has a capacity is 470 KW.

## Slide 26
Chiller:
For the building the total cooling load is equal 272.23kw, so the minimum capacity for the chiller should be equal to:
272.23x1.1=300 kw, we select chiller that fits the needs, in tons units=85.7 tons
Flow rate= 85.7*2.4=210.48 GPM and 50 HZ.
From the figure below we select the chiller of model W P S a 135-2D

## Slide 27
Fan coil units:
Sample 2nd floor:
Fan04
1000 Cfm
DC P 10 H/C 3

## Slide 28
Circulation pumps for chiller
S series S55 with 258.688 Pa/m and 6.5 L/s flow rate
Hot water pump demand = 28.5 GPM pressure= 6Psi
Potable water pumps:
From last chapter(plumping) we calculate the total demand cold water of the building which is equal=51.17 GPM pressure=6.7 Psi
Fire water pumps:
According to number of risers which equal 1
Now:
Flow rate=500 GPM
Pressure= 128.4 PSI
Jocky pump = 128.4+10=138 .4 Psi