## Slide 1: An-Najah National University
Faculty of Engineering
Civil Engineering Department
Graduation Project
Analysis and redisgn of Zawata
Water distribution
network
Prepeared by:
Nidal Safarini
Supervisor:
Dr. Anan Jayyousi

## Slide 2: Introduction:

## Slide 3: Facts:
Recomended consumption 100 L/C.d
Avrage Palestenian consumption is 70 L/C.d
Water recources are decreasing as people numbers incresing
Increase in demand
Lack of accessibility to clean water recources
High losses

## Slide 4: Objectives:
Analyse the existing network by collecting data
Build a model for it
Redisgn it

## Slide 5: Study area:

## Slide 6: Study area:
Number of residents 2000 in 2010
Temprature 9.4 in January and 26.5 in August
Humidity is about 50% in may minimum and 71% maximum in january and february
Avrage rainfall is 658mm
Avrage consumption 77 L/C.d

## Slide 7
Chart: No. Of residents
| 8 | 7 | 5 | 2 | 10 | 7 | 2 | 8 | 5 | 5 | 11 | 2 | 9 | 5 | 7 | 7 | 8 | 4 | 9 | 6 | 6 | 5 | 1 | 5 | 6 | 10 | 8
 | 54.1667 | 61.9048 | 66.6667 | 83.3333 | 16.6667 | 47.619 | 166.6667 | 125 | 133.3333 | 53.3333 | 60.6061 | 83.3333 | 74.0741 | 60 | 80.9524 | 71.4286 | 95.8333 | 166.6667 | 74.0741 | 83.3333 | 27.7778 | 120 | 166.6667 | 80 | 38.8889 | 150 | 41.6667
Average consumption with family size

## Slide 8
Chart: 
| Exellent | V.good | Good | bad | V.bad
 | 3 | 2 | 6 | 8 | 8
Satisfaction of water quantities supplied

## Slide 9
Chart: 
| Exellent | V.good | Good | bad | V.bad
 | 33 | 22 | 26 | 15 | 4
Satisfaction of the quality of water provided (%)

## Slide 10
Chart: 
| Exellent | V.good | Good | bad | V.bad
 | 11 | 7 | 22 | 30 | 30
Satisfaction of water price (%)

## Slide 11: Network characteristics:
Source is Nablus municipality
Pipe material is cast iron
The network is old
A reservoire is built
Fed twice weekly
Population density is 3.92 Capita/dunum

## Slide 12: Network map:

## Slide 13: Calculations:
AUTOCAD map.
Numbering nodes.
Numbering pipes.
Deviding area.
Assign node contribution on each area.
Calculate demand on each node.
Building a model on EPANET program.

## Slide 14: EPANET program
Is a modeling program.
Reservoirs.
Tanks.
Junctions (Nodes).
Pipes.
Pumps.
Valves.

## Slide 15: Steady state analysis
Minimum pressure head is 129 m.
Maximum pressure head is 193 m.
Minimum speed is 0 m/s.
Maximum speed is 0.37 m/s

## Slide 16: Unsteady state analysis
Pattern multiplier is 3.6.
Minimum pressure head is 31 m.
Maximum pressure head is 102 m.
Minimum velocity is 0.01 m/s.
Maximum velocity is 1.41 m/s.

## Slide 17: Future network design
Growth rate 2%.
Future population in 2040 will be 3623 capita.
Future population density 8 capita/dunum.
Future demand 100 l/c.d.

## Slide 18: Results on the existing network
Minimum pressure head is -91 m.
Maximum pressure head is -4 m.
Minimum velocity is 0.01 m/s
Maximum velocity is 3.35 m/s

## Slide 19: Results after changing pipe diameters
Minimum pressure is 4 m.
Maximum pressure is 65 m.
Minimum velocity 0.11 m/s
Maximum velocity 1.93 m/s.
Cost of the modified network is 309000 JD.

## Slide 20: Designing a new network
The old network is worn out.
Doesn´t represent the reality.
Doesn´t cover the future inhabited areas.
There is need to redesign a new network

## Slide 21: New network map

## Slide 22: Results of the new network
Minimum pressure head 2 m.
Maximum pressure head 119 m.
Minimum velocity 0.08 m/s.
Maximum velocity 1.86 m/s.
Cost of the new network will be 542500 JD.

## Slide 23: Thank you for listening