## Slide 1
Prepared By:
Rawand Jimlan
Reem Dalbah
Supervisor: Dr. Abed Alrahim Abu safa
July 5th -2024
Annajah-National University
Faculty of Enginering
Energy&Environmental Engineering Department
Integrated Geothermal cooling and Heat Recovery with Advanced AHU For a Wedding Hall in Jenin
Graduation Project 2

## Slide 2
Contents
01
02
03
04
05
06
07
Objectives
Introduction
Changing the system reason
Proposed system
Methodology
Feasibility analysis
Conclusion
08
System Design

## Slide 3
Objectives
Objective 01
.
Study and design the system including air handling unit, geothermal loop, chiller
and pump for cooling requirements.
Implement a comparison between water-cooled and air-cooled chillers and with and without heat recovery.
Select the effective and financially feasible chiller for the system.
Objective01
Objective02
Objective03

## Slide 4
Introduction
The domestic sector in Palestine is the largest consumer of energy by 60%, followed by the services sector and the commercial sector consumes 26%,65% of electricity consumption in both the domestic and commercial sectors in Palestine goes to heating and air conditioning systems. The number of devices used now is many times greater than it was ten years ago which became a necessity in all places, that increased the demand for electrical energy. Due to the Palestinians reliance on non-renewable energy sources such as fossil fuels, the environmental pollution has increased. It also poses a threat to these sources because they are non-renewable, so the sustainable alternatives should be the best option for these problem .In Palestine, 18% of total energy is renewable inclduing geothermal.

## Slide 5
to
Changing the system
.
geothermal heat pump with VRF
Integrated Geothermal cooling and Heat Recovery with Advanced AHU
Benefits of the new system
Combining a geothermal heat exchanger with a chiller, AHU, and heat exchanger for cooling a wedding hall offers significant advantages. The geothermal system provides a stable heat , reducing the chiller's load and lowering energy consumption and costs. The heat exchanger recovers waste heat, enhancing AHU efficiency and reducing energy demand. This integrated system is more energy-efficient, sustainable, and reliable than conventional systems, minimizing environmental impact and operational costs. However, it has a high initial cost

## Slide 6
Proposed system

## Slide 7
  Methodology:
Design Calculations
Economic analysis
  Location
  Soil thermal properties
  Weather and climate
  Pipe sizing for GHE
  AHU selection
  Chiller selection calculation
  Pump selection
  Duct sizing
  GHE selection
  SPP
  NPV
  IRR
  SIR
Site Evaluation

## Slide 8
Site evaluation
System Design
Knowing the location of the hall in Jenin city, its area is 900 square meters, and the available area around it is about one dunam, and weather information and the thermal properties of the soil, such as Thermal conductivity , thermal diffusivity , heat capacity

## Slide 9
Cooling load calculations
System Design
Total cooling load was estimated to be 348 kW for each zone taking into account building, doors, windows and ventilation.

## Slide 10
AHU selection:
System Design
Selected AHU without HR system is PAH 250 with 25000 CFM, 6 rows with cooling rated capacity of 1374.02 MBH.
Selected AHU with HR system is PAH 200 with 20000 CFM, 6 rows with cooling rated capacity of 608 MBH.

## Slide 11
System Design
Chiller selection
Water-cooled chiller: Selected chiller without heat recovery is EWWQ-L-SS (model 380) with rated capacity of 386.8 kW, power input of 87 kW and 4.446 COP.
Selected chiller with heat recovery system is EWWQ-G-SS (model 130) with rated capacity of 136, power input equals to 30.5 kW and a COP of 4.5.
Air-cooled chiller: Selected chiller without HR is EWYQ-F-XS (model 380) that has rated capacity of 376kW, power input of 129 kW and 2.91 COP.
Selected chiller with HR is EWYQ-G-XR (model 140) with rated capacity of 139, COP of 3.1 and power input of 50.2.

## Slide 12
Pump selection
System Design
Pump selection: according to chiller’s flowrate chiller using equation:
Then calculated L pipes by estimating the longest pipe length and multiplying it by 1.5.
From the performance curve for the pump, we chose its type S55 based on the flowrate and chose the pressure difference so that the delta P/L value is greater than 200 and less than 550.

## Slide 13
pump’s pipe
System Design
Pump’s pipes selection: according to the chart:

## Slide 14
Grilles and diffusers selection
System Design
depending on flowrate that has been calculated according to :
and number of diffusers:

## Slide 15
Duct sizing using Dutulator
System Design

## Slide 16
Geothermal pipes
  we calculated the diameter of the pipes based on flowrate.
  calculating the thermal resistances of the pipe, soil, convective to calculate the length of the geothermal pipes based on the following equation:
System Design
Without heat recovery, the length of the loop was 1080 meters ​, needed about 200 meters square area.
With heat recovery, it became 400 meters and occupies an area of ​​133 square meters

## Slide 17
economic analysis
System Design
Comparing the system when using water-cooled chiller, air-cooled chiller:

## Slide 18
economic analysis
System Design
Comparing the system when using water-cooled chiller, air-cooled chiller:

## Slide 19
economic analysis
System Design
Comparing the feasibility of the system with and without Heat recovery

## Slide 20
economic analysis
System Design
Comparing the feasibility of the system with and without Heat recovery

## Slide 21
Conclusion:
Heating and air conditioning systems are essential due to climate change and other factors. The proposed cooling system for the wedding hall in Jenin, integrating geothermal cooling and heat recovery technologies, offers a highly efficient, cost-effective solution, reducing energy costs significantly compared to an air-cooled chiller. With a positive net present value (NPV), a 11% internal rate of return (IRR), and substantial present value (PV) savings, this system supports sustainable building practices and exemplifies a robust, energy-efficient model.

## Slide 22
THANK YOU