## Slide 1
An-Najah National University | 2025
College of Engineering and Information Technology
Department of Energy Engineering and Environmen
Simulation of a Solar Assisted Heat Pump System for Heating An-Najah National University Closed Swimming Pool.
Supervisor: Dr. Abdalrahim Abusafa
Students name:
Aseel Amarni
Naheel Shtiwi
Sajed Methqal
Tamara Sawalha

## Slide 2
Swimming Pool Heating:
Swimming pool heating is essential for maintaining comfortable water temperatures year-round. Choosing the most efficient and sustainable method ensures energy savings and environmental benefits.

## Slide 3
Objectives:
Quantify thermal losses in the pool system under varying conditions and propose reduction strategies.
Thermal Losses Analysis
Design a hybrid solar-assisted heating system integrating collectors, heat pumps, and storage for efficient pool heating.
System Design
conduct an economic assessment covering costs, payback period, and comparison with conventional heating.
Economic Analysis
Assess environmental benefits by estimating emission reductions and supporting sustainability goals.
Environmental Impact Assessment
To simulate the control strategy of the hybrid system using MATLAB/Simulink, ensuring optimal performance.
Control System Simulation
Ensure user comfort with stable water temperature and design for future scalability.
Thermal Comfort and Scalability Improvement

## Slide 4
Swimming Pool Heating Systems:
1
2
3
Fossil fuel heaters
One of the most popular ways to heat a pool is with gas heaters.
Electric heaters
Easy to install and efficient for small spaces, but may consume significant electrical power over extended use.
Solar Pool Heater
It uses sunlight for heating—very sustainable but sunlight-dependent.
4
5
Heat pumps
Hybrid Pool Heating Systems
It relies on harnessing heat from the air or ground, making it an energy-saving and environmentally friendly option.
Hybrid systems combine solar, gas, or heat pump for efficient, smart heating.

## Slide 5
Solutions to improve the efficiency of swimming pool heating:
Fiberglass insulation procedures:
Pipe insulation is essential for pool heating.
Benefits:
Application
steps:
Pool Covers (Passive Heating Support):
While not a heating system
Benefits:
Cover the basin when not in use.

## Slide 6
PROBLEM STATEMENT
CURRENT SYSTEM ANALYSIS
SEARCHING FOR SOLUTIONS
PROPOSED SOLUTION:
CHOOSING THE BEST SYSTEM:
COMPARISON OF SYSTEMS:
CASE STUDY:
RetScreen
  It requires detailed information (such as heat pump size) and does not allow accurate simulation without prior experience, making it impractical.
  We decided to build our own algorithm using MATLAB and Excel to analyze the scenarios more accurately.
  We designed several systems and compared them economically and environmentally.
  We chose the system that achieves the best balance between economic efficiency and reduced environmental impact.
  High operational cost
  environmental pollution in the current system.
  Data analysis showed excessive fuel consumption, far more than needed to compensate for thermal losses
  We started using TRNSYS but couldn't find the required components.
TRNSYS
  Current University Swimming Pool Heating System
Methodology:

## Slide 7
Case Study:
Temperature: 45°C
Average volume withdrawal: 200 l/day
Temperature setting: 29 °C
Length: 25 m
Width: 12.5 m
Average depth: 12.5 m

## Slide 8
Effects of incomplete combustion on system cleanliness and efficiency
Smoke deposits impair combustion, increase energy losses and reduce operational efficiency.

## Slide 9
Evaluation and analysis methodology for a hybrid heating system
using:
RETScreen program:
Excel:
MATLAB:
RETScreen
MATLAB
Excel

## Slide 10
RETScreen program:
A platform developed by Natural Resources Canada for planning, analyzing, and monitoring low-cost renewable energy and energy efficiency projects.
Application features:
1
2
3
4
Project Feasibility & Financial Analysis:
Performance Analysis:
GHG Emission Analysis:
Decision Support:

## Slide 11
Why was Excel used as an analysis tool?
why wasn't it sufficient on its own?
Excel allows data to be entered and broken down into hourly intervals
Accurate Time Control:
Excel :
Dynamic Heat Loss Analysis:
Excel thermal equations estimate heat loss and hourly energy needs year-round.
Flexibility to Modify and Customize:
The model can be tailored to the geometric characteristics of the pool and surrounding building
Excel allows you to enter real climate data or import it from external sources.
Better integration
with real-world data:
Data presentation lacks
clarity and interactivity.
Excel displays results in the form of tables and numbers, which makes analyzing trends and detecting errors more difficult.
Lack of support for complex
dynamic modeling (loops):
Excel struggles with simulating feedback loops and component interactions.

## Slide 12
MATLAB:
MATLAB was chosen for its advanced capabilities for accurate data processing and analysis, along with its ability to provide dynamic visualization and support for complex algorithms.
Advanced Methods for Presenting Results
Powerful Data Control
MATLAB allows us to create custom and clear graphs that make results easier to understand.
We can manipulate data using accurate and effective feedback.
Ability to Use Complex Equations and Algorithms
MATLAB supports the implementation of precise algorithms for more professional data analysis.
Displaying Data Over Different Time Periods
Data can be represented over multiple time periods to understand performance evolution or changes.
Creating a Large Number of Graphs
Provides powerful visual tools for presenting and analyzing data from different perspectives.

## Slide 13
Hybrid Heating System Evaluation: MATLAB vs. Excel:
FEATURE
MATLAB
EXCEL
Purpose
Full hybrid system design, simulation, and optimization were performed.
Simplified thermal loss and cost analyses were carried out.
Complexity
High – control strategies and physical modeling were included.
Medium – formula-based calculations were utilized.
Data Processing
Loops, conditions, and weather file parsing were used.
Direct formulas and structured worksheets were employed.
Customization
Multiple user scenarios were supported.
Focus was placed on insulation and cover impact analyses.
Outputs
Graphs, CSV files, and economic metrics (NPV, IRR) were generated.
Direct numerical values, basic graphs, and payback periods were produced.

## Slide 14
MATLAB vs Excel Simulation Results
M
M
E
E
660,288.48 kWh
TOTAL LOSSES
144,431.26 kWh
PRODUCTIVE SOLAR ENERGY
542,375.23 kWh
TOTAL LOSSES
157,184 kWh
PRODUCTIVE SOLAR ENERGY
Total Losses
Productive Solar Energy

## Slide 15
Data collection:
  Environmental and solar radiation data based on geographic location were obtained from Solcast (a DNV company), a reliable source for high-resolution solar resource information.
Location-Based Environmental Data Collection
To ensure accuracy in our solar energy analysis, we selected the precise location of An-Najah National University in Nablus, using its geographic coordinates:
Latitude: 32.227551
Longitude: 35.220625
Using Solcast (a DNV company), we extracted high-resolution, hour-by-hour environmental data for this site, including:
  Different types of solar radiation
  Ambient temperature
  Solar zenith angle
This data enabled us to perform detailed analysis tailored to the specific climatic and solar conditions of the site.

## Slide 16
Solar Radiation and Air Temperature visualized data from RETScreen.
Daily Solar Radiation (kWh/m²/day)

## Slide 17
Data collection:
A screen shot from Geomolg showing the Available areas for solar collector installation.
The GeoMolg tool was used to determine the available space on the building's rooftop.
Total usable area: 300 square meters
Total perimeter: 74.37 meters
Actual area allocated for installation (after accounting for maintenance corridors and safe distances): 280 square meters
Reasons for reducing effective space:
  The need to provide safe maintenance aisles.
  Ensuring easy access to equipment for routine maintenance.
  Compliance with technical safety requirements.

## Slide 18
Evaporation (NWH): 20.12
Shower Demand (WH) 5.93
Pipes (NWH): 5.86
Walls (NWH): .6
Radiation (NWH) 5.74
Evaporation (WH): 27.92
Convection (NWH): 10.05
Pipes (WH): 6.52
Walls (NWH): .67
Radiation (NWH) :6.52
Evaporation (WH): 10.07
Convection Loss (20.12%): 20.12
Radiation Loss (12.26%): 12:26
Walls Loss (1.27%):1.27
Pipes Loss (12.38%) 12:38
Evaporation Loss (48.04%) 48.04
Working Hours Demand: 57.63
Non-Working Hours Demand: 42.37
Data collection:
Total Energy Demand:100
Total Shower Demand: 5.93
Total Losses: 94.07
376364kwh
283924kwh
660,288.48 kWh

## Slide 19
Convection Heat Coefficient (hc)
Results :
Improve the efficiency of the thermal system by insulating the pipes and using a pool cover.
  the Effect of Pool Cover on Heat Transfer Coefficients:
Parameter
Uncovered Pool
Covered Pool
10 W/m²·K
3 W/m²·K
Evaporation Heat Coefficient (he)
25 W/m²·K
5 W/m²·K
Impact of Pool Cover
Significant reduction (↓70%) in convective heat loss, enhancing thermal efficiency.
Major reduction (↓80%) in evaporative heat loss, decreasing energy consumption.

## Slide 20
The role of the cover in reducing heat losses:
Hourly Total Losses during Non-Working Hours (Subsampled)
Total Loss (No Cover)
Total Loss ( Cover)
Convection (No Cover)
Convection (Cover)
Evaporation (No Cover)
Evaporation (Cover)
Radiation
Walls
Pipes
Hourly Detailed Losses during Non-Working Hours (Subsampled)
Total Losses (kW)
Detailed Losses (kW)

## Slide 21
More heat lost → lower efficiency → higher energy use and costs
Less heat lost (↓29%) → improved efficiency → lower energy consumption
Condition
Thermal Conductivity
Heat Loss (Qpipe)
Without Insulation
Higher
13 W
With Insulation
Reduced
9.2 W
Impact on System Efficiency
Results :
  Effect of Pipe Insulation on Heat Loss and System Efficiency

## Slide 22
Analysis of energy loss in water heating system during working and non-working hours
397804kwh

## Slide 23
Strategies for compensating for heat loss during pool downtime
Max Pump Output:
Uniform Operation
173.34
8667.10
25.06
Pump Cost:
Pump Lifetime
Early Start
Max Pump Output:
193.12
9656.10
30.37
Pump Cost:
Pump Lifetime
Cyclic Operation
22.95
7877.59
157.55
Max Pump Output:
Pump Cost:
Pump Lifetime
Preheat
25.06
6907.13
138.14
Max Pump Output:
Pump Cost:
Pump Lifetime
Full Night Operation
16.10
6726.11
134.52
Max Pump Output:
Pump Cost:
Pump Lifetime

## Slide 24
Comprehensive thermal analysis of system losses over time periods.
Total Hourly Losses
Time (Hours)

## Slide 25
The efficiency of the solar collector increases with increasing temperature and decreases with increasing zenith angle.
Efficiency vs. Zenith Angle and Temperature
Simulation of Angle and Temperature Effects on Solar Collectors
The highest solar production (3 × 10⁵ kWh) is achieved at an inclination of 30°–40° and an azimuth close to 0°, while it decreases at extreme angles due to poor sun exposure.
Solar Energy vs. Tilt & Azimuth Angles

## Slide 26
Max
Mean
Min
Probability Distribution of Solar Collector Efficiency
Displays basic statistical values ​​for efficiency:

## Slide 27
Pump Energy Demand After Solar Energy Compensation.
The figure shows how solar energy contributes to covering a large part of the pump's consumption.
Minimum Q solar: 0.53 kWh
Maximum Q solar: 84.62 kWh
Average Q solar: 44.92 kWh
☀️
⛅
🌧️
Maximum Q losses:198.45 kW
Average Q losses: 49.9 kWh
Maximum Q pump:194 kW

## Slide 28
monthly heat loss profile.
Energy KWH
Monthly Solar Energy Production
Energy KWH
Monthly solar energy production and heat losses

## Slide 29
Winter
Spring
Summer
Autumn
🔥 Summer
🍂 Autumn
It achieved the highest surplus of 53.23% thanks to the abundance of solar radiation and long daylight hours.
It recorded a good surplus of 31.71% thanks to the balance between temperature and radiation.
🌨️ Winter
🌼 Spring
The lowest surplus was recorded over the year at 0%, reflecting weak solar inspections in the quarter.
Provide a moderate surplus of 15% due to increased radiation hours and improved weather conditions.
Seasonal Solar Surplus
(kWh)

## Slide 30
Engineering Diagram of the Solar Heating System.
Thermal storage tank:
Capacity: 6.01 cubic meters
The system contains two heat pumps, each with a capacity of 97 kilowatts thermal (kWth).
The average coefficient of performance (COP) for the pumps is estimated at 5.

## Slide 31
Energy Flow Diagram of the Hybrid Heating System.
The system consists of two air-to-air heat pumps, each with a capacity of 97 kW, with an average Coefficient of Performance (COP) of 5.
Thermal storage tank:
Capacity: 7 cubic meters
The system also includes an 85 kW water-to-air heat pump, and the average Coefficient of Performance (COP) for the entire system is 8.

## Slide 32
  Temperature Variations in the System
Dynamic Variations in the Performance of the Hybrid Heat Pump System
  Thermal Energy Stored in the Tank
  Coefficient of Performance (COP) of the Heat Pump
  Solar Collector Mass Flow Rate

## Slide 33
Seasonal Contribution of Each Source (Hybrid Heat Pump)
Distribution of Source Dependency in the Hybrid Heat Pump System: Monthly, Seasonal, and Annual Analysis.
Air
Water
Monthly Contribution of Each Source (Hybrid Heat Pump)
Annual Contribution of Each Source (Hybrid Heat Pump)
Contribution (%)
Contribution (%)
Contribution (%)

## Slide 34
Heat pump
Solar
Contribution (%)
Heat Pump: Source Contribution (Solar vs Heat Pump)
Contribution (%)
air
water
Hybrid Heat Pump: Source Contribution (Water vs Air)
Heat Pump vs. Hybrid Heat Pump: A Comparison
Annual Performance Comparison between Heat Pump System and Hybrid Heat Pump System.

## Slide 35
Smart control system for efficient heating using solar energy and heat pump

## Slide 36
Cumulative Savings summary by RETScreen.
Savings Cumulative
Actual
Predicted
Savings
Total GHG emissions predicted, actual and savings by RETScreen software.
RETScreen Overview: GHG Emissions and Cumulative Savings

## Slide 37
38400
Installation
Equipment
12000
89.4857
12000
2000
Insulation
Control System
3000
3000
2000
4000
Thermal Storage
Cover
6600
4000
6600
66000
Operating Cost
+Maintenance(USD)
Total
6164
60000
30613
Item
Heat Pump (HP)
Hybrid Heat Pump
Electric Heater
Diesel Boiler
Gas Boiler
Developed System
32400
21400
437.329
0
12000
4000
2000
86800
4000
8500
5383
12000
12000
12000
49000
3000
3000
3000
2000
2000
2000
4000
4000
4000
6600
6600
6600
51000
17600
41264
14109.54
46551
Analysis of the cost of different heating systems and their operation

## Slide 38
Annual Savings by System (Compared to Highest Cost System)
Type of Heating System
Annual Savings (USD)
The graph illustrates that both the heat pump and hybrid heat pump systems offer the highest annual savings, positioning them as the most cost-effective heating solutions among the compared systems.

## Slide 39
Pairwise Annual Savings Difference Between Various Heating Systems
Heat Pump vs Hybrid Heat Pump
Heat Pump vs Electric Heater
Heat Pump vs Diesel Boiler
Heat Pump vs Gas Boiler
Heat Pump vs Existing System
Heat Pump vs Upgraded System
Hybrid Heat Pump vs Electric Heater
Hybrid Heat Pump vs Diesel Boiler
Hybrid Heat Pump vs Gas Boiler
Hybrid Heat Pump vs Existing System
Hybrid Heat Pump vs Upgraded System
Electric Heater vs Diesel Boiler
Electric Heater vs Gas Boiler
Electric Heater vs Existing System
Electric Heater vs Upgraded System
Diesel Boiler vs Gas Boiler
Diesel Boiler vs Existing System
Diesel Boiler vs Upgraded System
Gas Boiler vs Existing System
Gas Boiler vs Upgraded System
Existing System vs Upgraded System
savings difference in US
*10⁴

## Slide 40
Annual CO₂ Footprint and Tree Offset for Pool Heating Options
number of trees required for compensation
tons/year
CO2 emissions

## Slide 41
772.561
Electric Heater
Hybrid Heat Pump
Heat Pump
Diesel Boiler
Gas Boiler
Return on Equity
Break-even
Existing System
Upgraded System
590.969
792.634
872.995
1046.2
0
1899.2
89.4857
78.3286
437.329
591.629
218.671
1770
669.3
Break-even Subscriptions and Return on Equity Analysis

## Slide 42
Comprehensive Comparison of Heating Systems
HEAT PUMP
55.5
HYBRID
51.5
ELECTRIC
31.8
42.8
55
52.2
DIESEL
GAS
DEVELOPED
Total

## Slide 43
Integrated Simulation of Swimming Pool Heating System with Solar Collectors and 3D Visualization
  The panel represents the data input and numerical results of a basin heating system simulation, showing the effect of environmental and structural variables such as the angle of inclination and the number of collectors on the system performance.
  It displays an interactive 3D simulation interface of a swimming pool heating system, enabling the user to adjust parameters and monitor real-time results such as efficiency, energy losses, and final tank temperature.

## Slide 44
Thank You
Innovation is seeing change as an opportunity, not a threat.