## Slide 1
Structural analysis and design for Burj Al-Jame’a - Jenin
By:
1. Mohammad Abbadi
2. Nafe’ Alyat
3.Omar Abd El-Jawad
Under supervision of:
Dr. Munther Diab
Graduation Project II
December 2018

## Slide 2
1 Project description.
2 Seismic Design Parameters.
3 Check for Structural Irregularities.
4 Structural System Type.
5 Preliminary Evaluation.
.
7 Three Dimensional Structural Analysis.
8 ETABS Model Checks.
.
Outline
9 Design Structural Elements
.

## Slide 3
Project Description
A commercial building located in Jenin, Palestine.

## Slide 4
Project Description
The soil in the site has a bearing capacity of about 3.5 kg/ cm2
Floor Name | Function | Area () | Height (m)
Basemen ІІ | Parking | 1208.8 | 3.25
Basement І | Parking | 1208.8 | 3.35
Ground | Mall | 1208.8 | 5.56
First | Mall | 1208.8 | 5.46
Second | Clinics | 1208.8 | 3.38
Third | Offices | 1208.8 | 3.38
Fourth | Student dormitories | 1208.8 | 3.38
Fifth | Student dormitories | 1208.8 | 3.38
Sixth | Student dormitories | 1208.8 | 3.38
Total |  | 10,880 | 34.52
Floor Name | Function |  | Height (m)
Basemen ІІ | Parking | 1208.8 | 3.25
Basement І | Parking | 1208.8 | 3.35
Ground | Mall | 1208.8 | 5.56
First | Mall | 1208.8 | 5.46
Second | Clinics | 1208.8 | 3.38
Third | Offices | 1208.8 | 3.38
Fourth | Student dormitories | 1208.8 | 3.38
Fifth | Student dormitories | 1208.8 | 3.38
Sixth | Student dormitories | 1208.8 | 3.38
Total |  | 10,880 | 34.52

## Slide 5
Materials
Non Structural
Structural
Tile (𝛾 = 25kN/𝑚3 )
Block (𝛾 =12 kN/𝑚3 )
Plaster
(𝛾 = 23 kN/𝑚3 )
Concrete Mortar
(𝛾 = 23kN/𝑚3 )
Filler
(𝛾 =16 kN/𝑚3 )
Concrete
Reinforcement
steel
. Stone (𝛾 = 27 kN/𝑚3 )

## Slide 6
Materials
Element | Value
Columns | 28 MPa
Shear walls | 28 MPa
Beams | 24 MPa
Footings | 24 MPa
Slabs | 24 MPa
Stairs | 24 MPa

## Slide 7
The Codes used in this project are the following :
  ACI 318-14 (American Concrete Institute).
1
  UBC 97 (Uniform Building Code).
2
The Codes Used in This Project

## Slide 8
Live Load
Parking (2.5 )
Mall (3.5 )
Clinics & Offices (3 )
Student dormitories (2 )
Super Impose Dead Load
(4 )
Slab Own Weight (6)
Gravity loads
Weight of Brick Wall
(1 )

## Slide 10
Seismic Design Parameters
R= 5.5
𝑪𝒂 = 0.24
&
𝑪𝒗 = 0.32
Ω = 2.8
Seismic Zone Factor,
Z = 0.2
Soil Profile Type ()
Importance Factor,
I = 1.0
Seismic Design Parameters

## Slide 11
Seismic Analysis Methods
1) Equivalent lateral force analysis
2) Modal response spectrum analysis
3) History analysis

## Slide 12
Check for Structural Irregularities

## Slide 13
Horizontal Irregularities
Vertical Irregularities
1a – Torsional Irregularities
1b – Extreme Torsional Irregularities
2 – Re-entrant Corners
3 – Diaphragm Discontinuity
4 – Out-of-plane Offsets
5 – Nonparallel Systems
1a – Stiffness Irregularity -Soft Story
1b – Stiffness Irregularity - Extreme Soft Story
2 – Weight (Mass) Irregularity
3 – Vertical Geometry Irregularity
4 – In-plane Discontinuity in Vertical Lateral Force Resisting Elements
5a – Discontinuity in Lateral Strength- Weak Story irregularity
5b - Discontinuity in Lateral Strength- Extreme Weak Story irregularity

## Slide 14
Horizontal Irregularities
In x-direction :
1a. Torsional Irregularity
1b. Extreme Torsional Irregularity
Story | Drift δ (mm)
Sixth | 27.64
Fifth | 24.54
Fourth | 21.03
Third | 17.38
Second | 13.68
First | 10.02
Ground | 4.21
B1 | 0.51
B2 | 0.19
Avg. | 13.24

## Slide 15
Horizontal Irregularities
In y-direction :
1a. Torsional Irregularity
1b. Extreme Torsional Irregularity
Story | Drift δ (mm)
Sixth | 23.32
Fifth | 20.07
Fourth | 16.91
Third | 13.76
Second | 10.68
First | 8.07
Ground | 3.86
B1 | 1.20
B2 | 0.38
Avg. | 10.92
Note: Extreme Torsional Irregularity exists.

## Slide 16
Horizontal Irregularities
2.Reentrant Corner Irregularity
Irregularity exist If: &

## Slide 17
Horizontal Irregularities
3. Diaphragm Discontinuity Irregularity
x
y
A
B
Occurs if: X*Y > %50 A*B

## Slide 18
Horizontal Irregularities
4. Out-of-Plane Offset Irregularity.

## Slide 19
Vertical Irregularities
1b. Stiffness-Extreme Soft Story Irregularity
1a. Stiffness-Soft Story Irregularity

## Slide 20
Vertical Irregularities
In x-direction :
Story | Load Case | Stiffness X kN/m
Sixth | EQXS | 933556.672
Fifth | EQXS | 1544241.98
Fourth | EQXS | 1948428.417
Third | EQXS | 2283244.209
Second | EQXS | 2605530.936
First | EQXS | 1879245.597
Ground | EQXS | 3211747.547
B1 | EQXS | 26667333.629
B2 | EQXS | 52425746.181
Fifth floor is soft story,

## Slide 21
2. Weight (Mass) Irregularity
Vertical Irregularities
Mass irregularity shall be considered to exist where the effective mass of any story is more than 150% of the effective mass of an adjacent story.
Story | Weight kN
Sixth | 15159.1
Fifth | 15108.2
Fourth | 15108.2
Third | 15108.2
Second | 15108.2
First | 17562.9
Ground | 17597.1
B1 | 17652.1
B2 | 17459.3
Note: No mass irregularity.

## Slide 22
Vertical Irregularities
3. Vertical Geometric Irregularity

## Slide 23
All of the above shows that the building is irregular. So, It is preferred to analyze the building dynamically using Response Spectrum method, that is suitable for all cases whether the building is regular or not .

## Slide 24
Preliminary Evaluation

## Slide 25
The selected system is two – way solid slab.
Selected slab system:
Slab

## Slide 26
Slab thickness calculated based on the critical span
Slab
For Solid Slab: Assume < 2
=Ln (0.8+Fy/1400)/ (36+9B) 90 mm
B= (long clear span/shorter clear span)
B= (7.2)/ (5.3) =1.36
h=7.2(0.8+420/1400)/ (36+9*1.36) =0.16 m
h= 200 mm. But, for Seismic reasons use h= 250 mm

## Slide 27
For all floors, the Beam distribution is shown:
1
Beams distribution
Beams

## Slide 28
Beams
2
Beams dimensions
In X & Y direction the critical beam is one end continuous
Depth =
Width =
Use Depth = 650 mm
Width = 400 mm

## Slide 29
Beams
2
Beams dimensions
Opening Beams
We use the secondary beams in order to reduce the slab deflection near openings, so we suppose dimensions to be:
Depth = 250 mm
Width = 300 mm

## Slide 30
Columns
For all floors, the distribution is shown:
Columns distribution
1

## Slide 31
Columns
2
Dimension of column
The chosen column is C9, which has a tributary area equal 3 the average ultimate slab weight = 15.33 for all floors.
For Seismic reasons use 1000*550 mm.
For circular columns in we supposed diameter = 900 mm – will be rechecked in design phase. Also, some columns shall be minimized, especially the edge ones.

## Slide 32
Shear Walls
For all floors the distribution was:
Shear wall distribution

## Slide 33
Shear Walls
For all floors the distribution was: For axial capacity, from ACI318-14 code, the axial capacity of the wall is given by the following equation:
Pu on shear wall = load from slabs + own weight
∅𝑃𝑛 = 0.55∅𝑓𝑐′ 𝐴𝑔[1-] where, K: Effective length factor from ACI 318-14 table 11.5.3.2, take K = 0.8.
Lc: Maximum vertical length of wall from center to center of joints. = 5.56 m
∅= 0.7, 𝑓𝑐′=24,
h:Wall thickness = 0.3 m .
Ag: Cross section area
Shear wall checks

## Slide 34
Shear Walls
If Pu < ∅𝑃𝑛 , Shear Wall dimension will be adopted.
Shear wall checks

## Slide 35
Three Dimensional Structural Analysis

## Slide 36
ETABS Model Checks
Compatibility
Drawing structural model
External equilibrium
Internal equilibrium
Slab shear
Fundamental period
Base shear by ELM
Structural system type
Mass participation ratio
Base shear by Response Spectrum
Slab deflection
Drift
Checks

## Slide 37
ETABS Model Checks
Drawing structural model
1

## Slide 38
2
ETABS Model Checks
Compatibility
All structural members are moving as one unit.

## Slide 39
Load type | Manual results (kN) | ETABS results (kN) | Difference %
Dead | 141792 | 145864 | 2.79 %
Live | 30042.2 | 30067.7 | 0.08 %
3
ETABS Model Checks
External Equilibrium
All loads on the structure and reactions are approximately the same.

## Slide 40
4
ETABS Model Checks
Internal Equilibrium ( for frame )
Make a check on Ground floor slab for Live load ( = 3.5 kN/
Manual Value:
== = 121.41 kN.m
ETABS Value:

## Slide 41
ETABS Model Checks
5.a
Slab shear (V13)
Ø= 0.75 ××√fc `×b×d×
Ø = 0.75× ×√ 24× 1000× 220×
= 134.72 kN/m
V13 = 29.796 kN/m
Ø= 134 kN/m > = 29.796 kN/m

## Slide 42
ETABS Model Checks
5.a
Slab shear (V23)
Ø= 0.75 ××√fc `×b×d×
Ø = 0.75× ×√ 24× 1000× 220×
= 134.72 kN/m
V13 = 28.733 kN/m
Ø= 134 kN/m > = 28.733 kN/m
 Slab thickness is adequate.

## Slide 43
Fundamental period
ETABS Model Checks
6
Code:
Ta = Ct
= 0.048
= 0.69 sec
Upper limit of period = Cu*Ta
=1.4*0.69
= 0.966 sec
ETABS:
Fundamental period = 0.907 sec < 0.966 sec

## Slide 44
Structural system type
ETABS Model Checks
7
Building Frame System (concrete shear walls).
R = 5.5
= 2.8

## Slide 45
Mass participation ratio
ETABS Model Checks
8
Number of modes taken to develop design spectra must have at least 90% of the participation mass of the structures for each principle direction as reported in both UBC 97 and IBC codes. In this project, the first nine modes - using Ritz Modal Case Sub Type - participate in more than 90% of the mass for both directions.
TABLE: Modal Participating Mass Ratios |  |  |  |  |  |  | 
Case | Mode | Period, sec | UX | UY | Sum UX | Sum UY | Sum RZ
Modal | 1 | 0.907 | 0.5581 | 0.0328 | 0.5581 | 0.0328 | 0.0378
Modal | 2 | 0.765 | 0.0356 | 0.6005 | 0.5937 | 0.6333 | 0.0378
Modal | 3 | 0.663 | 0.0395 | 0.003 | 0.6332 | 0.6363 | 0.6103
Modal | 4 | 0.222 | 0.1057 | 0.0011 | 0.7389 | 0.6374 | 0.6157
Modal | 5 | 0.163 | 0.0001 | 0.14 | 0.739 | 0.7774 | 0.6298
Modal | 6 | 0.14 | 0.015 | 0.0296 | 0.7541 | 0.807 | 0.7282
Modal | 7 | 0.113 | 0.0383 | 0.0036 | 0.7923 | 0.8106 | 0.7371
Modal | 8 | 0.064 | 0.1593 | 0.0208 | 0.9516 | 0.8314 | 0.7376
Modal | 9 | 0.061 | 0.023 | 0.1357 | 0.9746 | 0.9671 | 0.7385

## Slide 46
Base Shear by Eq. Static Method
ETABS Model Checks
9
kN
kN
Manual
ETABS
So, It is Acceptable

## Slide 47
Base shear by Response Spectrum
ETABS Model Checks
9
Input data of Response Spectrum

## Slide 48
Base shear by Response Spectrum
ETABS Model Checks
9
Results of current dynamic analysis
Results of modified dynamic analysis

## Slide 49
ETABS Model Checks
10
Slab deflection
Check was Implemented on the critical panel in Ground Floor.
Δ Allowable = L/240 =9.62/240 = 0.040m = 40mm
Deflection from ETABS = 22.40 mm
Deflection from ETABS < allowable deflection
Acceptable

## Slide 50
Design of Structural Elements

## Slide 51
Structural Design
Beams
Slabs
Shear walls
columns
Footings
Stairs
Design

## Slide 52
Slabs Design
1
Check slab thickness for Shear
Shear capacity for the slab.
Ø= 0.75 ××√fc `×b×d×
= 0.75× ×√ 24× 1000× 220×
= 134.72 kN
Vu = 29.796 kN
Ø= 134 kN > = 29.796 kN
 Slab thickness is acceptable.
Slabs

## Slide 53
In x-direction :M11
< 29.50  use
As =0.0018× 1000×220 = 726
Use 1ø14/20 cm, Bottom in x direction.
Slabs

## Slide 54
In y-direction :M22
Slabs
< 29.50  use
As =0.0018× 1000×220 = 726
Use 1ø14/20 cm, Bottom in y direction.
shrinkage steel:
As (shrinkage) = 0.0018x1000x250 = 450mm2
4Ø12/m
But, use = 1Ø12/20 cm (in both directions)
.

## Slide 55
Steel Detailing In Slab
Slabs

## Slide 56
Columns
Columns distribution

## Slide 57
Code ACI318-14 permits to neglect the slenderness in braced columns if :
≤ 34 – 12
≤ 40
Where:
K: the effective length factor.
Lu: the unsupported height.
r: the radius of gyration which equals to , where I is the moment of inertia and A is the area of the section.
M1: Smaller factored end moment on column.
M2: larger factored end moment on column.
Slenderness check
Columns

## Slide 58
Check slenderness on column C5 in two direction
Assume k=1
Lu = 5.46m
r = 0.3h = 0.3*1 = 0..30m
= = 18.20
18.20 ≤ 34 – 12* = 37.40
≤ 40
Neglect slenderness.
Slenderness check
Columns

## Slide 59
Reinforcement percentages
All values are permitted as ACI318-14.
Columns

## Slide 60
ACI requirements of columns
Columns

## Slide 61
Summery of columns
Columns

## Slide 62
Summery of columns
Columns

## Slide 63
Detailing of column group C-1

## Slide 64
1
Beams Design
Design of beam for flexure:
Left moment value  M=308.31 kN.m
Mid. Moment value  M= 172.90 kN.m
Right moment value  M= 377.57 kN.m
For the mid of span M+ = 172.90 kN.m
(use 5Ø16)
For the right and left side of span is
maximum value of M- = 377.57 kN.m
(use 7Ø20)
Beams

## Slide 65
1
Beams Design
Design of beam for shear force:
Left shear value  V=234.77 kN
Right shear value  V=241.84 kN
Shear Rebar Ratio (Av/S):
Concrete shear Capacity is found using :
ØVc =0.75* * b*d = **400*590/1000
=144.525 kN
Vu =234.77 kN
Vu > ØVc we need stirupps
Use =150 mm  6Ø10/m
At distance 2h from support: Vu =163 kN
S = d/2 = 300 mm 3Ø10/m.
Beams

## Slide 66
2
Beams Detailing

## Slide 67
1
Shear wall design
Shear Wall

## Slide 68
For vertical and horizontal reinforcement:
Shear Wall
Internal forces in shear wall:
Vu = 2867 kN
Mu = 20424 kN
Pn = 8665 kN
vertical :  AS= Use 1Ø16/200mm
horizontal :  AS= Use 1Ø14/200mm

## Slide 69
Shear Wall
Shear Wall Detailing:

## Slide 70
Mat Footing
Single
Footing
Combined Footing
Piles
Wall
Footing
Design of footing

## Slide 71
Footing
Mat Footing was selected
Allowable bearing pressure is small q all =350kN /.
Area of single footings and wall footings in the base is more than half ground floor area.
Required area of footing =
Required area of footing = = 624
Area of basement = 1210
Percentage between required area of footing and area of basement equals 0.515, which is greater than 0.50.

## Slide 72
Design of footing

## Slide 73
Design of footing
Compatibility:
 A𝒄𝒄𝒆𝒑𝒕𝒂𝒃𝒍𝒆
Deflection :
Δallowable= 𝑞𝑎𝑙𝑙𝑜𝑤𝑎𝑏𝑙𝑒/k
= 350/(350*100)= 0.01 m = 10 mm
Δallowable=10 > Δmax=9.4 mm
 A𝒄𝒄𝒆𝒑𝒕𝒂𝒃𝒍𝒆
Punching Shear:
The ratio of punching shear = (Vu/ΦVcp) < 1
 A𝒄𝒄𝒆𝒑𝒕𝒂𝒃𝒍𝒆
Checks for mat footing
Checks for thickness of 1.1 meter

## Slide 74
Punching shear check
ФVcp
ФVcp = 6598 kN
Vup <<< ФVcp
Design of footing
Interior column
 A𝒄𝒄𝒆𝒑𝒕𝒂𝒃𝒍𝒆

## Slide 75
Design of footing
Mat Foundation Reinforcement:
= 0.0018 * 1000* 1100 = 1980
= (1980 *420) / (0.85 * 24 * 1000) = 40.764
= 1980 * 420 * ( 1040 – 20.38) * = 847.91 KN.m
ΦMn = 0.9 * 847.91 = 763.12 KN.m

## Slide 76
Design mat footing (M11)
Design of footing
Design mat footing (M22)

## Slide 77
Mat Foundation Reinforcement:
Design of footing
Then As = As, min =1980 mm2 φ20/15 cm
but we will take it φ25/15cm to achieve the value for
area under column and shear walls.
For both X & Y Directions.

## Slide 78
Detailing in mat Footing

## Slide 79
Design of stairs
acceptable
Thickness of the flight according to ACI code :
in our project we use it 0.17 m  17 cm
Load Calculations :
For flight  Wu =
For Landing  Wu=

## Slide 80
Design of stairs
Check shear
ØVc =0.75* * b*d
= **1000*150/1000 =122.47 KN
ØVc >
So we don’t need shear reinforcement
Steel design :
For flight :  for moment  AS= 2053.6  1Φ16\10 cm
for  AS= 1026.8  1Φ16\20 cm
For flight :  ( top & bot )  As = 759  1Φ14\20 cm
Shrinkage steel:  As= 306 1Φ10\25cm

## Slide 81
Longitudinal section
Design of stairs

## Slide 82
Thank you