## Slide 1
Granulation Project 2
MECHANICAL SYSTEMS IN BUILDINGS
IBN SENA HOSPITAL
Prepared by:
Abdullah Hasayen
Mazin Khalid
Moath Ayyash
Mohammad Abu Al-Rub
Supervisor:
Dr. Ramiz Al Khaldi

## Slide 2: In our project we will design the following mechanical systems:
Heat Ventilation and air conditioning (HVAC) system in IBN SENA Hospital.
Plumping system in IBN SENA Hospital .
Fire fighting in IBN SENA Hospital .

## Slide 3: Building Description
IBN SENA HOSPITAL building located in jenin city, which consists of four floors. Basement floor, ground floor, first floor, and second floor . Each floors have more one room such as patients rooms, doctors rooms, isolations rooms, and ICU rooms.

## Slide 4
HVAC means that Heat Ventilation and Air Conditioning system .
The main objective of air conditioning is to maintain the environment in enclosed space at conditions that achieve the feeling of comfort to human.
HVAC System

## Slide 5
winter:
Outside temperature (To) be 5.7 ˚C.
Inside temperature (Ti) be 22 ˚C.
Outside Relative humidity (Фo) is 72% .
Inside Relative humidity (Фi) is 50%.
Outside Moisture content (Wo) is
8.2 g of water/ Kg of dry air.
Inside Moisture content (Wi) is
4.2 g of water/ Kg of dry air.
SUMMER :
Outside temperature (To) be 31.9 ˚C.
Inside temperature (Ti) be 24 ˚C.
Outside Relative humidity (Фo) is 44.
Inside Relative humidity (Фi) is 50%.
Outside Moisture content (Wo) is
12.5 g of water/ Kg of dry air.
Inside Moisture content (Wi) is
9.4 g of water/ Kg of dry air
Inside and Outside Condition

## Slide 6
Heating load
calculation

## Slide 7
The Required UVER All Heat Transfer

## Slide 8
The following equations were used to calculated the heating load:
Qs,cond = U A (Tin – To) .
Q s,vent = 1.2 Vvent (Tin – To).
Q l,vent = 3 Vvent (Wi- W o).
Qtotal = Qs,cond + Qs,vent +Ql,vent .
Heating Load Equations

## Slide 9
No. of | Q (total) | Q (total) Ton | Q (total) CFM
Floor | kw |  | 
Basement floor | 54.396 | 15.534 | 9967.65
Ground floor | 166.585 | 47.5957 | 30540.58
First Floor | 174.515 | 49.861 | 31994.45
Second Floor | 186019.6 | 53.148 | 34103.59
HEATING LOAD RESULTS

## Slide 10
The boiler is the main source of heating process, selection of boiler depends on its capacity. selection of boilers from De Dietrich company.
The total amount of heat in our project equal to 580.4 KW.
Total heating = [Q)Heating load +Q)domestic]*1.1
Total heating = (580+480)*1.1 = 1166 KW
.
From De Dietrich catalogue we choose the boiler
GT530 DIEMATIC-m3

## Slide 11
Cooling load
calculation

## Slide 12
Cooling load calculated at summer season.
Cooling design conditions (in summer):
Outside temperature (To) be 31.9˚C.
Inside temperature (Ti) be 24 ˚C.
Outside Relative humidity (Фo) is 44%.
Inside Relative humidity (Фi) is 50%.
Outside Moisture content (Wo) is 12.5 g of water/ Kg of dry air.
Inside Moisture content (Wi) is 9.4 g of water/ Kg of dry air.
The wind speed at JENIN is (5 m/s).
Cooling Load

## Slide 13
Qs = U * A * CLTD corc CLTD coro = ( CLTD + LM ) K +( Tin -25.5 ) + ( To – 29.4 ). Qs) transmitted = A * SHG * SC * CLF . Qs) convection = U * A * ( CLTD ) correction. Qs) vent = 1.2 *A * ( To – T in ) . Q latent = 3 * A ( W o –W in )
Qs) people = qs * n * CLF Ql) people = ql * n Qs) lighting = W * CLF Qs) equipment = qs * CLF Ql) equipment = ql
Cooling Equations

## Slide 14
Q : heat loss ( watt) .
U : over all heat transfer coefficient (w/m2.k).
Tin : inside temperature (C) .
To : outside temperature ( C ).
LM : Latitude correction factor .
SHG: Solar heat gain .
SC :shading coefficient .
CLF : cooling load factor .
CLTDcorr : The correction of cooling load temperature difference.
n: number of people.
W: lighting capacity.
Q vent : the heat losses due to sensible ventilation .
Definition for term of Previous Equations

## Slide 15
No. of | Q (total) | Q (total) Ton | Q (total) CFM
Floor | kw |  | 
Basement floor | 75.99 | 21.48 | 13931
Ground floor | 190.342 | 54.38 | 34896
First Floor | 236.283 | 67.5 | 43318
Second Floor | 288.793 | 82.51 | 52945
COOLING LOAD RESULTS

## Slide 16
The chiller is the main source of cooling process, our selection depends on PETRA COMPANY.
The Total sum of cooling load =225.87*1.1= 247.5 Ton
So we select 435 ton R 134-a chiller it's manufactured with two compressors and with the same compressors type.
The Chiller Code is: WPS a 220 2 S

## Slide 17
DUCT DESIGN
Grills are calculated and distributed uniformly.
The duct is drawn and distributed before
Calculations
The sensible heat of floor is calculated.
The initial velocity is 5 m/s.
And then we use ductulator software
As shown in figure.

## Slide 18
PIPE DESIGN
The total cooling load was calculated for the floor.
The mass flow rate for the water calculated (m).
The pressure head was estimated in (Kpa) .
The longest loop from the boiler to the far fan coil unit and return to the boiler was calculated multiplying by (1.5) due to fittings.
The pressure head per unit length is calculated and it should be between range from (200< ∆p/L<550).
Then the diameter of pipe entering to the floor is estimated

## Slide 19
FAN COIL UNITS SELECTION
The fan coils units are selected from PETRA COMPANY, the catalogue of Petra Company are used to selections depending on the air flow rate (cfm)
Selection Code from (catalogue I):
This code from (catalogue I) used to selection the flow rate from (200 cfm to 1200 cfm).
Fan coil for first room in second floor:
Vcirculation = 476L\s = 671.385 CFM, we select
DC10 FCU..

## Slide 20
There are many type of fixture that used in the building and there size of every pipe in the fixture are establishing from the international standard code.
Plumping System in Building

## Slide 21: The plumping fixture unit in building
Type of fixture | No. of fixture | Size of pipe (in)
Water closet ( w .c ) | 5 | 1/2 , 3/8
Lavatory | 2 | 1/2 , 3/8
Kitchen sink | 2 | 1/2
Shower head | 4 | 1/2

## Slide 22
In potable water system :
1-collector system were used in design of plumping system.
2-PVC were used for cold water services pipes in building .
3- CPVC were used for hot water services pipes in building.

## Slide 23
There are many type of fixture that used in the building and there sizes of every pipe in the fixture are mentioned, they are establishing from the international standard code.
Drainage System in the Building

## Slide 24
Type of fixture | No .of fixture | Size of pipe(in)
Water closet | 4 | 4
Lavatory | 1 | 2
Kitchen sink | 3 | 2
Shower head | 2 | 2
Floor drain | 3 | 2
Drainage Fixture Unit in the Building

## Slide 25: The design of drainage system applied as follows:
1) Every stacks contains many fixture are groups and there are many no. of stacks in each floor , and every stack connected to the stories of the building because it is easily to work and collect waste , soil water from all stories .
2) The vent design of the stack pipes equal 2 in until reach the last floor it becomes equal 4 in , so that to obtain a good ventilation to drainage system in the building.

## Slide 26
3)the floor drain were put in path room and kitchen it is for collecting waste water from drainage system and the wash water of each floor and connect to stack directly .
4) Many manholes were put in the design because they are used for collecting the all drainage water from stack and connected to main house drain from municipality for push drainage water system to the municipality net pipe.

## Slide 27
Fire protection is the prevention and reduction of hazards associated with fire
Fire protection has major goals :
Life safety .
property protection .
Fire Protection

## Slide 28
The AFP falls into two categories.
Fire suppression: The fire is extinguished by manual or automatic means, such as a fire extinguisher .
Fire detection: The fire is detected either by locating the smoke or heat, and an alarm is sounded to enable emergency evacuation as well as to dispatch the local fire department.
Active Fire Protection