## Slide 1
Comfort amelioration forthe Faculty of Fine Arts
Prepared by:
Hamza Hamide
Motaz Hamarheh
Haytham sbitany
Supervisor:
Eng.Wala Omar

## Slide 2: Outline
Architectural Design
Environmental Design
Mechanical Design
Electrical Design
Quantity Surveying & conclusions
Structural Design

## Slide 3
Architectural Design
Notes: Before starting the comparison between the old and new design its important to mintion our stratigy of design that basicly depend on how achive the optimum functionalty of building , as you can see here some main added space to new design .

## Slide 4
Architectural Design
Original
Design
Site Plan
Notes: Starting with a comparison within the old site and the new site plan , that show clearly the location of the structure in an-najah new campus near to the main entrances , as you can see in the photo here .

## Slide 5: Architectural Design
Our
Design

## Slide 6
Architectural Design
Ground Floor
Original
Design

## Slide 7: Architectural Design
Our
Design

## Slide 8
Architectural Design
First Floor
Our
Design

## Slide 9
Architectural Design
Second Floor
original
Design

## Slide 10
Architectural Design
Second Floor
Our
Design
Notes: The new design of second floor staes green area for students

## Slide 11
Architectural Design
Third Floor
Our
Design

## Slide 12
Architectural Design
Fourth Floor
Our
Design

## Slide 13
Architectural Design
Fifth Floor
Our
Design
Notes: The new design of fifth floor contain a faculity gallery with 300 m sq

## Slide 14
Architectural Design
Elevations

## Slide 15
Architectural Design
North Elevation

## Slide 16
Architectural Design
West Elevation

## Slide 17
Architectural Design
South Elevation

## Slide 18
Architectural Design
East Elevation

## Slide 19
Architectural Design
Section
Section
A-A

## Slide 20
Architectural Design
3D Models

## Slide 21
Architectural Design
3D model

## Slide 22
Architectural Design
3D model

## Slide 23
Architectural Design
3D model

## Slide 24
Architectural Design
Egress Routs in G.F

## Slide 25
Structural Design

## Slide 26
Structural Design
Codes
(ACI 318) for RC Structures Design
(UBC 97) for Earthquake Loads
(ASCE 7 2010) for loads computations
(ACI 350.3-06) for Water Tanks Loads

## Slide 27
Structural Design
Loads
Live Load = 5 KN/
SID= 4 KN/m2
EQ Loads:
I= 1 Cv=0.2
R= 5.5 Ca=0.2
Z= 0.2 (2B) Ct= 0.563
Notes: These loads parameters were used in the programming the model of etabs

## Slide 28
Structural Design
Material
Concrete B350 for all structural elemants.
Concrete B150 for all blinding at footing level.
Notes: Moving to the material two kind of concret were used

## Slide 29
Structural Design
Blocks of the Building
Notes: This slide shows the different block in the project

## Slide 30
Structural Design
Block B/B of the Building
Notes: As you can here Block B/B were choosed to be designed

## Slide 31
Structural Design
Compatibility Check
Notes: Starting with the well done compatability check as you can see here

## Slide 32
Structural Design
Equilibrium Check
Load | Manual calculations (KN) | Calculations from SAP (KN) | Difference (%)
Dead load | 55575.68 | 58770 | 2.7
Live load | 23350 | 22902 | 0.24
Superimposed dead load | 31700 | 32186 | 0.016
Element | Hand calculations | Calculations from SAP | Difference (%)
Slab 1 | 365 KN.m | 344 KN.m | 5.70
Beam 6 | 1021 KN.m | 910 KN.m | 9.97
Column 5 | 4460 KN | 4555 KN | 1.23
Internal Forces Check
Notes: Continue The rest of checks that illustrated here

## Slide 33
Structural Design
Deflection
Notes: Finaly ending with the deflection check

## Slide 34
Structural Design
Fine Art Faculty
Two-way ribbed slab
Two way solid slab
Slabs
Beams
Columns
Footing
Stair case
Notes: This diagram here shows the relations between the structural elemats as usual

## Slide 35
Structural Design
Slab:
Two-Way Ribbed Slab with dropped beams
Notes: Two kinde of slabs were used the first one is

## Slide 36
Structural Design
Slab:
Two-Way SOLID Slab

## Slide 37
Structural Design
Beam Design (fram5)
Section 1-1
Section 2-2
Section 3-3
FRAM DESIGN
Notes: Moving to the beam design
All of beams were designed in a complete farams

## Slide 38
Structural Design
Column Design
Notes: This slide shows the sizmic column design

## Slide 39
Structural Design
Footing Design
Wall footing
Isolated footing

## Slide 40
Structural Design
Footing Design
Strip Shear wall Footing

## Slide 41
Structural Design
Continuous wall footing Design

## Slide 42
Structural Design
Isolated Footing Design

## Slide 43
Structural Design
Shear Wall Design

## Slide 44
Structural Design
Stair
Notes: Ending up with the stair reinforcement

## Slide 45
Environmental Design

## Slide 46
Double Glass U = 1.7
Certain Wall U= 2.2
External Roof U=0.31
External wall U=0.47
Internal Ceiling
U= 0.34
Ground Floor
U= 1.58
Notes: It should be noted here that the values of insulation were very poor in the old design, and the problems which it caused

## Slide 47
ACOUSTICAL DESIGN
RT60 in the Music Room

## Slide 49
RT60 in the Class Room.

## Slide 51
Sound Transmission Class (STC)
Classroom external wall

## Slide 52
Sound Transmission Class (STC)
Classroom internal wall

## Slide 53
IMPACT INSULATION CLASS (IIC)

## Slide 54
Shading
              Winter

## Slide 55
Shading
Summer

## Slide 56
Daylight Analysis
Ground Floor
Notes: Two sample were used to display the daylight distribution and the daylight factor in the faculty, which are the ground floor and the third floor

## Slide 57
Third Floor

## Slide 58
Thermal Loads
Total cooling load is 554.1 KW

## Slide 59
Total Heating load is 397 KW

## Slide 60
Thermal Comfort
The recommended acceptable PMV range for thermal comfort from ASHRAE 55 is between -0.5 and +0.5 for an interior space.
Notes: In our case, this rate has been achieved most of the year

## Slide 61
Mechanical Design

## Slide 62: Mechanical
Drainage system.
Water supply system.
Elevators.
Fire fighting system.
HVAC system.

## Slide 63: Plumbing Fixtures
Used plumbing fixtures in the project are:
Water closets.
Lavatories (also called bathroom sinks).

## Slide 64: Drainage system :
The main pipes are U.P.V.C with 4’’size and P.V.C 2’’ size for internal connection and 6’’ U.P.V.C for outdoor pipes.
All pipes (2’’,4’’ and 6’’ pipes) have slope equal to 1% to let the waste water flow by gravity.
The manholes are connected with the vertical, the last manhole is connected to the main sewer , The pipe’s size between the manholes is 6’’ to ensure good flow rate.
Type | Type |  |  |  |  | 
 | Black Water |  |  | Grey Water |  | 
 | Diameter | Slope | Type | Diameter | Slope | Type
Stack | 4'' | 0%(90°) | PVC | 4'' | 0%(90°) | PVC
Sewer | 4'' | 1% | PVC | 2'' | 1% | PVC
Drainage | _ | _ | _ | 4'' | 1% | PVC
Manhole Sewer | 6'' | 1% | PVC | _ | _ | _
Vent | 4'' | 0%(90°) | PVC | 4'' | 0%(90°) | PVC

## Slide 66: Water supply system :
The system is designed based on flush tank and public used for all fixture unit.
The cold water are supplied to the fixture unit(Lavatories) from the roof fresh tanks and the fixture unit (WCs) from the roof grey water tank.
There is a tank with 10m3 for recycle the water from lavatories and reusing it for flush tank (WCs) in each block in the basement floor ; to reduce water consumption.
The hot water supplied from the electrical water heater that fixed in each bath room .

## Slide 67
Total fixture units : 249 fixture unit in each block.
Total cold water consumption per month is 66 m3 and the same for hot water.
Total grey water consumption per month is 154 m3.
The cold water tanks supplied from a basement tank with capacity 80 m3, 30m3 for fresh water and the rest saving for fire fighting system .

## Slide 68: Elevators:
the best option is 3 elevators with 2500Ib / 350fpm , but we will use 4 elevators to achieve the uniformity in the faculty because we have two zone, in each zone two elevators .

## Slide 69: Fire fighting system:
Notes: this figure shows the fire fighting systems that designed as we see here fire hose station and the distribution of dedicators , audio visual alarm and fire exist sign

## Slide 70: Emergency Exits in The Building
Notes: This slide shows the emergency exits in the building this is for up floor and this is for ground floor

## Slide 71: HVAC system:
Based on the "Design Builder“ results of the total cooling capacity and the total heating capacity we designed based on the largest value which is cooling load capacity.
Then we used three outdoor unit with capacity 140 kw for each one outdoor unit to achieve the needed cooling capacity .
Notes: The Hvac system that used is vrf outdoor unit then

## Slide 72: HVAC system:
Notes: The hvac system that designed in the faculty is vrf system and this figure shows the distribution of diffuser in the ground floor as an example

## Slide 73
Electrical Design

## Slide 74
Studio for lithography and offset.
Artificial lighting
Notes: Artificial lighting ……… Dialux evo were used for these calculations …….. We have 2 rooms samples starting with …………… and we have got a 545lux Illuminance and uniformity of 0.68 and the Max UGR = 16.4 and its all in its acceptable ranges.

## Slide 75
Classroom:
Notes: A classroom room have 391 lux illuminance and uniformity of 0.65 and max UGR 17.9 so all values acceptable.

## Slide 76: Lighting distribution in GF

## Slide 77: Main boards

## Slide 78
Cost
Estimation

## Slide 79
Price(NIS) | Quintity | Unit | Work
1249851 | 3571,002 | m3 | Concrete works
550000 | 189,655 | Ton | Steel works
1322300 | 13223 | m2 | Form work
64427 | 1171,4 | m3 | Excavation work
326260 | 14830 | m2 | Plastering works
266940 | 14830 | m2 | Paint works
562800 | 8400 | m2 | Tile works
258090 | 8541 | NO. | Windows & doors
420000 | 1200 | m2 | Curtain wall
238000 | 6800 | m2 | False celling
634492,8 | 12040 | m2 | Block works
59040 |  |  | Staircase
1720035 |  |  | MECHANICAL
71947,29 |  |  | Electrical
7744182 | Total project cost (NIS) |  | 
922 | Total unit cost (NIS/m2) |  | 

## Slide 80
Mechanical Design

## Slide 81: Mechanical
Drainage system.
Water supply system.
Elevators.
Fire fighting system.
HVAC system.

## Slide 82: Plumbing Fixtures
Used plumbing fixtures in the project are:
Water closets.
Lavatories (also called bathroom sinks).

## Slide 83: Drainage system :
The main pipes are U.P.V.C with 4’’size and P.V.C 2’’ size for internal connection and 6’’ U.P.V.C for outdoor pipes.
All pipes (2’’,4’’ and 6’’ pipes) have slope equal to 1% to let the waste water flow by gravity.
The manholes are connected with the vertical, the last manhole is connected to the main sewer , The pipe’s size between the manholes is 6’’ to ensure good flow rate.
Type | Type |  |  |  |  | 
 | Black Water |  |  | Grey Water |  | 
 | Diameter | Slope | Type | Diameter | Slope | Type
Stack | 4'' | 0%(90°) | PVC | 4'' | 0%(90°) | PVC
Sewer | 4'' | 1% | PVC | 2'' | 1% | PVC
Drainage | _ | _ | _ | 4'' | 1% | PVC
Manhole Sewer | 6'' | 1% | PVC | _ | _ | _
Vent | 4'' | 0%(90°) | PVC | 4'' | 0%(90°) | PVC

## Slide 85: Water supply system :
The system is designed based on flush tank and public used for all fixture unit.
The cold water are supplied to the fixture unit(Lavatories) from the roof fresh tanks and the fixture unit (WCs) from the roof grey water tank.
There is a tank with 10m3 for recycle the water from lavatories and reusing it for flush tank (WCs) in each block in the basement floor ; to reduce water consumption.
The hot water supplied from the electrical water heater that fixed in each bath room .

## Slide 86
Total fixture units : 249 fixture unit in each block.
Total cold water consumption per month is 66 m3 and the same for hot water.
Total grey water consumption per month is 154 m3.
The cold water tanks supplied from a basement tank with capacity 80 m3, 30m3 for fresh water and the rest saving for fire fighting system .

## Slide 87: Elevators:
the best option is 3 elevators with 2500Ib / 350fpm , but we will use 4 elevators to achieve the uniformity in the faculty because we have two zone, in each zone two elevators .

## Slide 88: Fire fighting system:
Notes: this figure shows the fire fighting systems that designed as we see here fire hose station and the distribution of dedicators , audio visual alarm and fire exist sign

## Slide 89: Emergency Exits in The Building
Notes: This slide shows the emergency exits in the building this is for up floor and this is for ground floor

## Slide 90: HVAC system:
Based on the "Design Builder“ results of the total cooling capacity and the total heating capacity we designed based on the largest value which is cooling load capacity.
Then we used three outdoor unit with capacity 140 kw for each one outdoor unit to achieve the needed cooling capacity .
Notes: The Hvac system that used is vrf outdoor unit then

## Slide 91: HVAC system:
Notes: The hvac system that designed in the faculty is vrf system and this figure shows the distribution of diffuser in the ground floor as an example

## Slide 92
Electrical Design

## Slide 93
Studio for lithography and offset.
Artificial lighting
Notes: Artificial lighting ……… Dialux evo were used for these calculations …….. We have 2 rooms samples starting with …………… and we have got a 545lux Illuminance and uniformity of 0.68 and the Max UGR = 16.4 and its all in its acceptable ranges.

## Slide 94
Classroom:
Notes: A classroom room have 391 lux illuminance and uniformity of 0.65 and max UGR 17.9 so all values acceptable.

## Slide 95: Lighting distribution in GF

## Slide 96: Main boards

## Slide 97
The new redesign solved the arrangement of the spaces according to standards and create new spaces that has not been found in the previous design such as; cafeteria and gallery..etc
The heat transfer coefficient for the walls and ceilings improved. Also, the northern façade has been utilized to improve the daylight in the building, so, the natural lighting has been solved in contrast previous design .
The tie beams have not been found in the previous design and after the redesign the tie beams are placed.
Conclusion

## Slide 98
The structural system converted from one way ribbed slab without secondary beams into two way ribbed slabs with secondary beams .
The HVAC system used in the building was sufficient enough to overcome the previous cooling problems .
The storm water collected in a tank and utilized for irrigation and both the grey water and the fresh water was separated .
The number of elevators changed to fit the number of people in the faculty.