## Slide 1: Redesign Of Integrated Car showroom
Prepared By :
Basheer Ibrahim
Emad Sokkar
Mutaz Dawood
Sameh Abu Aishih
Supervisor:
Eng. Fadi Fatayer

## Slide 2: Outline
Architectural Design
Structural Design
Environmental Design
Mechanical Design
Electrical Design
Safety Design
BOQ
Site location

## Slide 3: Site Information
The site is located at Nablus city, Beit- Iba Street. slight slope.
The land has an area = 7936.2m2.

## Slide 4: Outline
Architectural Design
Circulation and entrances
Comparison between suggested and final plan
Elevations
Site plan
Sections

## Slide 5
The suggested design for our project is one of a student work of the third year of architectural department.
During our project we modified the
selected design (redesign the model)
In order to be suitable for the
selected site in Nablus city.

## Slide 6: Comparison between suggested &final Design

## Slide 7: Cars storage

## Slide 8: Ground Floor
Total Area = 1550m2

## Slide 9: First Floor
Total Area = 1630 m2

## Slide 10
Site plan
Circulation &entrance
Area total=7936 m2

## Slide 11: East & west Elevation
West elevation
East elevation

## Slide 12: North & south Elevation
South elevation
South elevation

## Slide 13: section A-A

## Slide 14: section B-B

## Slide 15: Outline
Environmental Design
Shading Design
Daylight factor
Thermal analysis
Acoustical design
Photovoltaic cells

## Slide 16
Building in ecotect

## Slide 17
At 9:00 AM
At 12:00 PM
Shading at 21June
At 4:00 PM
shadow range for the building from 8:00 am to 18:00 pm every half hour.

## Slide 18
12vertical Adjustable
Louvers - 30 cm
Fixed cantilever – 29 cm.
West and East
South
Showroom
perforated panel perforation ratio of 40.3%

## Slide 19
Before shading
After shading in summer
After shading in winter
General Office shading - South

## Slide 20
Daylight factor
Daylight factor in = 5.26%
Autonomy =83.46%
GF of showroom

## Slide 21
Daylight factor in F.F of showroom= 5.20%
Autonomy =87.26%
Daylight factor in General office = 4.81%
Autonomy =91.56%

## Slide 22
Materials :
External wall of U = 0.48 W/m2.K

## Slide 23
Curtain wall of U = 1.1 W/m2.K
(6mm Stop Sol- 16mm Argon – 4 mm planibel)

## Slide 24
Internal wall of U = 2.57 W/m2.K

## Slide 25: Materials :
Roof of U = 0.38 W/m2.K

## Slide 26
Ceiling of U = 0.36 W/m2.K

## Slide 27
Ground Floor of U = 0.43 W/m2.K

## Slide 28
Heating/cooling loads in showroom
Max Heating: 31950 W at 13:00 on 18th January
Max Cooling: 193054W at 12:00 PM on 31th July

## Slide 29
Heating/cooling loads in Dealer office
Max Heating: 925 W at 11:00 on 19th January.
Max Cooling: 1797 W at 14:00 on 23rd July.

## Slide 30
Heating/cooling loads for all building
Max Heating: 54092 W at 13:00 on 18th January.
Max Cooling: 229175 W at 12:00 on 31st July.

## Slide 31: Reverberation Time RT60 in showroom
The optimum reverberation time for showroom is (1-1.4)sec ,
We used tow perforated false ceiling with different absorption coefficient for ground and first floor to optimize RT60

## Slide 32
Absorption coefficient for ground floor ceiling
Absorption coefficient for first floor ceiling.
Reverberation time inside showroom after improving.

## Slide 33
RT60 before any improvement
RT60 after applying the improvements

## Slide 34
STC for ceiling =84 db.
Layers | STC (dB)
20cm Hollow Block (medium) | +48
Insulation in air gap | +3
Plaster to one sides | +2
Total | 53
STC for external wall =53 db.
STC Values:

## Slide 35
we use photovoltaic cells of type CS6K obtained from Canadian solar manufacture with nominal power of 270 W
Photovoltaic

## Slide 36: Photovoltaic
Horizontal portrait installation
Simulation of horizontal portrait instillation
Produced energy=49.94 MWh/year
Performance ratio=82.5%

## Slide 37: Outline
Structural Design
Design cods
Design Data
Structural Elements
Etabs Result
Detailing

## Slide 38: The structural systems
Two structural systems were used in the project:
Concrete Structure.
Truss Steel structure

## Slide 39: Design Codes
The American Concrete Institute code (ACI 318-11).
The seismic design according to UBC-97.
The analysis and design were done using SAP2000, and ETABS 2015 programs.

## Slide 40: Design Data
1. Concrete compressive strength
f’c =24 MPa for slabs and footings.
f’c =28 MPa for shear walls, columns and beams.
2.Yielding strength of steel
The yield strength of steel Fy= 420MPa
3. Bearing capacity of soil
the bearing capacity of soil = 150KN/m2

## Slide 41: Structural Systems concrete structure
Sold slab “Car exhibition Building”
Thickness :
Solid slab = 30 cm

## Slide 42: Structural Elements concrete structure:
Beams
Columns
Footing
Shear wall
Slabs
Stairs

## Slide 43: 3D Modeling ETABS 2015

## Slide 44: Checks ETABS 2015
Compatibility & Deflection Check:

## Slide 45: Checks ETABS 2015
Equilibrium Check

## Slide 46: Seismic Design Response Spectrum
  Base shear reaction:
W= 45802 KN , Include D.L+S.D+0.25LL
UBC-97
I = 1
R= 5.5
Ca= 0.280
Cv= 0.40
T = 0.324 sec

## Slide 47: Slab Reinforcement

## Slide 48: Footing Reinforcement

## Slide 49: Footing Reinforcement

## Slide 50: Stairs Reinforcement

## Slide 51: Shear wall Reinforcement

## Slide 52: Steel truss structure
Materials Design Data:
A36 steel with yielding strength (Fy) = 250 Mpa and ultimate strength (Fu) = 400 Mpa
Concrete with Fc' = 24 Mpa
Metal sheet with weight of 75 kg/m2
E70xx welding material, with strength F =480 Mpa.

## Slide 53: Loads
Values | Loads type
2 KN/m2 | live
.75 KN/m2 | SID
2 KN/m2 | Snow
.25KN/m2 | Wind load

## Slide 54: 2D – Model

## Slide 55: Compatibility check for truss

## Slide 56: Sections used in truss
We used HSS for all group in truss:

## Slide 57: Connection Design
Dimension of gust plate:

## Slide 58: Outline
Mechanical Design
Water supply system
Drainage system
HVAC

## Slide 59
Water consumption
Total building of water demand = 1792 g/ day
Functions | Gal.per day | Water consumption
Washing cars | 100-150 | 150
Employees | 12 | 12
Maintenance | 5-10 | 10
No Private bath (per persons) | 50 | 1000
Additional kitchen requirements | 10 | 20
showers | 600 | 600

## Slide 60
a water tank of 33 m3

## Slide 61
Total FU’s | Collector
92 | In maintenance
100 | In show room in GF
28 | In show room in FF
Meter of 3.00 in
vertical of 3 in
Horizontal of 2.5 in
branch of 2.00 in

## Slide 62
Drainage system for Ground Floor

## Slide 63
Roof and Storm water Drainage

## Slide 64: HVAC Design
The used HVAC system is VRF system

## Slide 65: We need 4 outdoor units of Mitsubishi type with 69KW (235400BTU/h) Cooling capacity.
Out door unit

## Slide 66
We used fan coils to receive natural air, supply air and to distribute the air through the Diffusers slot diffuser:

## Slide 67
Diffusers distribution:

## Slide 68
Main Duct sizing :
V’=1.98 m3/s , V=6m/s , (Δ𝑝/𝐸𝐿)=0.59 Pa/m

## Slide 69: Outline
Safety Design
Circulation
Safety signs
Fire Fighting System

## Slide 70: circulation movement and door exit

## Slide 71: Fire Fighting System
Sprinkler distribution In showroom.

## Slide 72: Fire Fighting System
Hose and extinguishers cabinet
Fire alarm device

## Slide 73: Safety signs
Emergency exit signs.
Don’t use the elevator in case of fire or earthquakes

## Slide 74
Outline
Architectural Design
Structural Design
Environmental Design
Mechanical Design
Electrical Design
Safety Design
BOQ
Site location
Socket distribution
Lighting distribution
Dialux

## Slide 75
Distribution of Sockets

## Slide 76
Outline
Architectural Design
Structural Design
Environmental Design
Mechanical Design
Electrical Design
Safety Design
BOQ
Site location
Socket distribution
Lighting distribution
Dialux

## Slide 77: Results calculations from dialux evo for showrooms
For showroom in ground floor (lx=1146>1000,Uo=0.66~0.70 and UGR=14<19)

## Slide 78: Results calculations from dialux evo for showrooms
For showroom in first floor (lx=1176>1000,Uo=0.68~0.70 and UGR=15<19)

## Slide 79: Type of lighting units used in showrooms
Unit type | Quantity | Specifications | Total
Philips Lighting DN570B PSED-E 1xLED40S/830 F 1xLED40S/830 | 115 in showroom 1 184 in showroom 2 | Light output ratio: 100% Lamp luminous flux: 4200 lm Luminaire Luminous Flux: 4200 lm Power: 38.0 W Light yield: 110.5 lm/W Colour temperature: 3000 K Color rendering index: 100 | 299
Philips Lighting 4ME450 P-WB 1xSON250W +9ME100 R GC D450 | 45 combined between showroom 1&2 | Light output ratio: 78.98% Lamp luminous flux: 27000 lm Luminaire Luminous Flux: 21324 lm Power: 276.0 W Light yield: 77.3 lm/W Colour temperature: 3000 K Color rendering index: 100 | 45
Philips Lighting MCS501 1xCDM-TEV35W EB 12_930 | 10 in showroom1 11 in showroom 2 | Light output ratio: 67.84% Lamp luminous flux: 4300 lm Luminaire Luminous Flux: 2917 lm Power: 43.0 W Light yield: 67.8 lm/W Colour temperature: 3000 K Color rendering index: 100 | 21

## Slide 80: Distribution of Lighting
Show room in GF
Showroom in first floor

## Slide 81: Artificial Lighting from Dialux.evoProgram
Show room rendering

## Slide 82: Artificial Lighting Dialux Program

## Slide 83: Sound reinforcement system
We used two types of loud speakers which is obtained from Yamaha company.

## Slide 84
Distribution of loudspeaker for ground floor of showroom.

## Slide 85
Distribution of loudspeaker, Sprinkler, Diffusers and lighting units togother.

## Slide 86: Outline
BOQ

## Slide 87: Bill of Quantities
Total cost of project= 4047462 $
Cost for the project with land price per m2= 1185 $/m2

## Slide 88
Thanks for your listening