## Slide 1
Architectural Aspect
Redesigned
1
PROJECT 2
Ground floor:
Administration offices need to organized.
First & second floor:
Grade one have an extra number of class than the grade two, and I don’t want this.
No need for two lobbies and two kitchens.
Toilets have a different location from ground floor and that will create a mechanical design problem in future, so to avoid these from happening we must put them in the same place.
Class number and area dose not matching with class in the above story and that
mean the school can’t include all this number of pupils for the next years.
The first floor escape stair has a bad door orientation.
Improvements that we make to the building. It can contain + 30 car and that cover all school needed for car parking.
Useless area in the corridor .
Basement floor:

## Slide 2
The ground floor before re-design:
2
PROJECT 2

## Slide 3
The ground floor after re-design:

## Slide 4
The first floor before re-design:
4
PROJECT 2

## Slide 5
The first floor after re-design:

## Slide 6
The second floor before re-design:
6
PROJECT 2

## Slide 7
The second floor after re-design:

## Slide 8
Basement Floor – As a modifier

## Slide 9
Areas
Total budgeted cost equal (without landscape) 1,242,786.37 JD.
Land area = 4727 m2.
Building area = 3466 m2
Cost Estimate
Total budgeted cost equal (building with landscape) 1,388,193.87 JD.

## Slide 10
Work done by: Lana Al-Hasan
Architectural and environmental Aspects
Pv system
HVAC system
Cost estimation and quantity surveying – for Architectural work
Presentation – Graduation Project 2

## Slide 11
3. Architectural & Environmental Aspects
Architectural- Case study
Architectural- 3D model design
Architectural- Landscape design
Environmental- Site analysis
Environmental- Shadowing and solar gain
Environmental- Daylight factor
Environmental- Heating and cooling loads
Environmental- Modification

## Slide 12
Architectural Aspects

## Slide 13
1.1 Case study analysis
Figure.1.01. Surrounding buildings
Figure.1.02. Site plan
Figure.1.03 North elevation
Figure.1.04 Shot from outdoor
Figure.1.05 Shot from outdoor

## Slide 14
Figure.1.07 Shot from indoor
Figure.1.09 Section - material
Figure.1.08 Shot from indoor
Figure.1.06 Section - doors

## Slide 15
Figure.1.10. North - Elevation
Figure.1.12. West - Elevation
Figure.1.13. East - Elevation
Figure.1.11 South - Elevation
2D - Before modifier - Elevations
1.2 Building model

## Slide 16
3D - Before Modifiers

## Slide 17
2D - After modifiers, Elevations
Figure.1.14. North - Elevation
Figure.1.15. South - Elevation
Figure.1.17. East - Elevation
Figure.1.16. West - Elevation

## Slide 18
3D - After Modifiers

## Slide 19
Materials Used for- After case
Green paint - exterior
Thickness: 1 mm
Tirol ™ Altra-teraco
Smoothed artificial stone
Thickness: 5 cm
Glazing system
Thickness: 6 mm – each layer
Double low e glass
Alucobond
Thickness: 3 mm
With aluminum cantilever frame
Painted concrete
Aluminum lovers

## Slide 20
Why using these colors ?

## Slide 21
1.3 Landscape – Before

## Slide 23
Landscape – After

## Slide 24
Materials Used for Landscape
Painted concrete as a floor & seats
Cement tiles
Ceramic landscape tiles
Gross
Flowers block – boundary

## Slide 26
Environmental Aspects

## Slide 27
8 am – for both winter and summer
2 pm– for both winter and summer
12 pm– for both winter and summer
2.1 Site analysis

## Slide 28
N
W
N
E
S

## Slide 29
Figure.2.38. North – West, Elevation
21.1
12 pm
Figure.2.37. North – East, Elevation
Figure.2.42. South – East, Elevation
Figure.2.43. South – West, Elevation
2.2 Shadowing and solar gain

## Slide 30
21.6
12 pm
Figure.2.29. North – East, Elevation
Figure.2.30.North – West, Elevation
Figure.2.31. South – East, Elevation
Figure.2.32. South – West, Elevation

## Slide 31
Season | Time | Shadowing effect |  |  | 
 |  | South-west elevation | North-east elevation | South-east Elevation | North-west elevation
Winter | 8:00 am | 1.01 | 0.48 | 0.89 | 0.44
 | 12:00 Pm | 1.18 | 0.84 | 1.02 | 0.71
 | 2:00 Pm |  |  |  | 
summer | 8:00 am |  |  |  | 
 | 12:00 Pm |  |  |  | 
 | 2:00 Pm |  |  |  | 

## Slide 32
Solar heat gain
Winter 21.1
Roof
North-West
North-East,

## Slide 33
South-West
South-East

## Slide 34
Summer 21.6
Roof
North-West
North-East,

## Slide 35
South-West
South-East

## Slide 36
Season | Time | Solar heat gain(KWh/m2) |  |  |  | 
 |  | South-west elevation | North-east elevation | South-east Elevation | North-west elevation | Roof
Winter | 8:00Am-2:00 Pm | 1.01 | 0.48 | 0.89 | 0.44 | 1.13
summer | 8:00Am-2:00 Pm | 1.18 | 0.84 | 1.02 | 0.71 | 3.89

## Slide 37
Before - modification
Heating Load = 265.80 Kw
Cooling Load = 315.50 Kw
Net Site Energy = 163.46 KWh/m2
Heating Load = 265.80 Kw
Cooling Load = 315.50 Kw

## Slide 38
1.
Change the school function design & HVAC system.
2.
3.
4.
5.
Applying shading system and revel only.
Wall insulation only.
Roof insulation only.
Windows glass treated only.
6.
Inside Curtin louvers with medium reflectivity only.
7
Photovoltaics system used only.
2.3 Environmental modification

## Slide 39
Before modification
Change school function and HVAC system.
Net Site Energy = 122.71 KWh/m2
Heating Load = 207.49 Kw
Cooling Load = 328.35 Kw

## Slide 40
Applying shading system and revel only.
Net Site Energy = 112.93 KWh/m2
Heating Load = 199.33 Kw
Cooling Load = 319.37 Kw
Wall insulation only.
Net Site Energy = 103.40 KWh/m2
Heating Load = 170.1 Kw
Cooling Load = 267.46 Kw

## Slide 41
Roof Insulation only.
Net Site Energy = 108.03 KWh/m2
Heating Load = 183.82 Kw
Cooling Load = 286.84 Kw
Inside curtain louvers with medium reflectivity only.
Net Site Energy = 110.98 KWh/m2
Heating Load = 191.08 Kw
Cooling Load = 303.10 Kw

## Slide 42
Glazing treated only.
Net Site Energy = 105.69 KWh/m2
Heating Load = 176.35 Kw
Cooling Load = 307.65 Kw
Photovoltaics.
Net Site Energy = 83.84 KWh/m2
Heating Load = 199.4 Kw
Cooling Load = 296 Kw

## Slide 43
After all modifications
Net Site Energy = 45.92 KWh/m2
Heating Load = 75.13 Kw
Cooling Load = 149.90 Kw

## Slide 44
Detailing
Walls detailing
Roof detailing

## Slide 45
Glazing system
Dbl LoE Spec Sel Clr 6mm/13mm Arg
Shading system
Long-wide alucobond cantilever
Aluminum cantilever
Horizontal louvers
30 cm revel With 20 cm frame window

## Slide 46
Thermal comfort
Annual comfort is in the range of 0.1 to -0.1

## Slide 47
monthly comfort is in the range of 0.5 to -0.5,

## Slide 48
finally that daily comfort is in the range of 1 to -0.5.

## Slide 49
Standard
(according to the mechanical and electrical equipment book N 40).
1.5 % * 9000 (the solar radiation reached from sun) = 135 lux
2.5 % * 9000 (the solar radiation reached from sun) = 225lux
Teaching spaces, art room, library and offices need nearly: 300 -350 lux (3.90 % : DF)
Corridors and stair case need nearly: 100 lux with white floor tiles and wall paints
Entrances: 200 lux
2.4 Daylight factor

## Slide 50
2.2 Daylight factor – Before
3D Mass by Revit
GF
FF
SF

## Slide 51
Daylight factor – After
3D Mass
GF
FF
SF
BF

## Slide 53
 | Zone | Design Capacity (kW) | Heating load (W/m2) | Total heating load (KW)
Ground Floor | Entrance | 2.02 | 39.840 | 62.646
Ground Floor | Kg-3 | 2.21 | 45.059 | 70.851
Ground Floor | Library | 1.83 | 39.933 | 62.792
Ground Floor | Corridor 2 | 1.5 | 23.374 | 36.754
Ground Floor | Multi-purpose room | 4.41 | 55.772 | 87.697
Ground Floor | Dining room | 6.61 | 102.513 | 161.193
Ground Floor | Secretary room | 0.7 | 34.965 | 54.979
Ground Floor | Food preparation area | 0.93 | 30.760 | 48.368
Ground Floor | Wc's | 0.62 | 27.249 | 42.847
Ground Floor | Art room | 1.64 | 29.023 | 45.636
Ground Floor | Kg-2 | 1.76 | 36.746 | 57.780
Ground Floor | Kg-1 | 2.28 | 52.688 | 82.847
Ground Floor | Wc's 1 | 0.48 | 16.076 | 25.278
Ground Floor | Accountant room | 0.81 | 32.964 | 51.833
Ground Floor | Regression | 0.77 | 34.588 | 54.387
Ground Floor | Manger room | 1.13 | 45.697 | 71.855
Ground Floor | Lobby | 3.82 | 63.333 | 99.587
Ground Floor | Parents meeting room | 1.26 | 57.399 | 90.255
2.5 Heating and Cooling Loads
Heating load

## Slide 54
 | Zone | Design Capacity (kW) | Heating load (W/m2) | Total heating load (KW)
First Floor | WC's | 0.56 | 22.735 | 35.749
First Floor | Wc's | 0.65 | 23.403 | 36.800
First Floor | Class9 | 1.42 | 50.480 | 79.375
First Floor | Class8 | 1.34 | 44.122 | 69.378
First Floor | Class7 | 1.6 | 52.000 | 81.766
First Floor | Class6 | 1.17 | 38.272 | 60.180
First Floor | Class5 | 1.57 | 53.445 | 84.038
First Floor | Class4 | 1.19 | 40.384 | 63.501
First Floor | Art room | 1.61 | 47.297 | 74.370
First Floor | Class3 | 1.57 | 53.843 | 84.663
First Floor | Class2 | 1.24 | 41.161 | 64.722
First Floor | Class1 | 1.53 | 53.419 | 83.996
First Floor | Teachers room | 1.83 | 34.906 | 54.887
 | Zone | Design Capacity (kW) | Heating load (W/m2) | Total heating load (KW)
Second Floor | Wc | 0.86 | 35.154 | 55.277
second Floor | Teachers room | 2.43 | 46.344 | 72.872
second Floor | Class9 | 1.82 | 62.679 | 98.557
second Floor | Class8 | 1.91 | 63.646 | 100.079
second Floor | Class7 | 1.79 | 61.553 | 96.787
second Floor | Class6 | 1.85 | 62.203 | 97.810
second Floor | Art room | 1.95 | 57.410 | 90.272
second Floor | Wc's | 1.15 | 43.218 | 67.957
second Floor | Class5 | 1.69 | 57.630 | 90.619
second Floor | Class4 | 1.83 | 58.409 | 91.844
second Floor | Class3 | 1.91 | 61.109 | 96.089
second Floor | Class2 | 1.94 | 62.985 | 99.038
second Floor | Class1 | 1.94 | 63.078 | 99.185

## Slide 55
 | Zone | Design Capacity (kW) | Total Cooling Load (kW) | Design Cooling (W/m2)
Ground Floor | Entrance | 2.65 | 2.3 | 52.2
Ground Floor | Kg-3 | 1.53 | 1.33 | 31.2
Ground Floor | Library | 3.27 | 2.85 | 71.5
Ground Floor | Corridor 2 | 4 | 3.48 | 62.2
Ground Floor | Multipurpose room | 3.77 | 3.28 | 47.6
Ground Floor | Dining room | 1.45 | 1.26 | 22.5
Ground Floor | Secretary room | 2.4 | 2.09 | 120.5
Ground Floor | Food preparation area | 4.95 | 4.3 | 164.1
Ground Floor | Wc's | 1.09 | 0.95 | 47.9
Ground Floor | Art room | 4.92 | 4.28 | 87
Ground Floor | Kg-2 | 5.79 | 5.04 | 120.7
Ground Floor | Kg-1 | 5.41 | 4.7 | 125.2
Ground Floor | Wc's 1 | 2.14 | 1.86 | 72.2
Ground Floor | Accountant room | 1.54 | 1.34 | 62.5
Ground Floor | Regression | 1.4 | 1.22 | 63.1
Ground Floor | Manger room | 2.56 | 2.22 | 103.2
Ground Floor | Lobby | 5.52 | 4.8 | 91.4
Ground Floor | Parents meeting room | 0.96 | 0.84 | 43.8
Cooling load

## Slide 56
 | Zone | Design Capacity (kW) | Total Cooling Load (kW) | Design Cooling (W/m2)
First Floor | WC's | 1.88 | 1.63 | 75.8
First Floor | Wc's | 1.83 | 1.59 | 65.5
First Floor | Class9 | 3.05 | 2.65 | 108.2
First Floor | Class8 | 2.87 | 2.5 | 94.9
First Floor | Class7 | 2.77 | 2.41 | 90.1
First Floor | Class6 | 3.5 | 3.05 | 114.6
First Floor | Class5 | 2.99 | 2.6 | 101.6
First Floor | Class4 | 5.49 | 4.78 | 185.8
First Floor | Art room | 4.73 | 4.11 | 139.2
First Floor | Class3 | 3.71 | 3.23 | 126.9
First Floor | Class2 | 4.09 | 3.55 | 135.3
First Floor | Class1 | 5.1 | 4.43 | 178.3
First Floor | Teachers room | 2.35 | 2.04 | 44.7
Table 2.36 Heating and Cooling Load (KW)
 | Zone | Design Capacity (kW) | Total Cooling Load (kW) | Design Cooling (W/m2)
second Floor | Wc | 2.57 | 2.23 | 105.3
second Floor | Teachers room | 3.99 | 3.47 | 76.3
second Floor | Class9 | 4.57 | 3.98 | 157.2
second Floor | Class8 | 3.94 | 3.43 | 131.5
second Floor | Class7 | 3.94 | 3.42 | 135.3
second Floor | Class6 | 4.6 | 4 | 155.1
second Floor | Art room | 4.65 | 4.04 | 136.9
second Floor | Wc's | 3.76 | 3.27 | 141.5
second Floor | Class5 | 3.7 | 3.21 | 126
second Floor | Class4 | 3.47 | 3.02 | 110.8
second Floor | Class3 | 3.55 | 3.09 | 113.9
second Floor | Class2 | 3.54 | 3.08 | 115
second Floor | Class1 | 3.91 | 3.4 | 127.1

## Slide 58: Structural Analysis
:General Information
Design code:
American Concrete Institute ACI 2014 for design.
Uniform Building Code (UBC 97) is adopted the code in Earthquake Analysis.
Materials
Concrete.
f´c = 32 Mpa for columns, walls and footings
f´c = 24 Mpa for slabs and beams
Reinforcement steel (Fy = 420 Mpa)

## Slide 59: Structural Analysis
General Information:
Loads
Live Load= 5 KN/m²
Superimposed dead load = 4 KN/m²
Dead load=5.74 KN / m².
External wall Load =20 KN /m.
One-way and two-way of 32cm-thickness ribbed slab will be used in this project according to every panel dimension.

## Slide 60: Structural Analysis
Seismic analysis:
Seismic zone : 2A with (Z = 0.15)
Soil profile : SC
Acceleration-dependent seismic coefficients Ca=0.15.
Velocity-dependent seismic coefficients Cv= 0.25.
Importance factor I=1.
Force reduction factor R=5.5

## Slide 61: Checks
Compatibility check
Equilibrium check
Internal Forces check
Deflection check
Period check
Base shear check
Drift check
All checks OK

## Slide 62: Slab Structural System
One way ribbed and two way ribbed
Thickness 32cm
Hidden beams and drop beams.

## Slide 63: Basement Slab

## Slide 64: Slab

## Slide 65: Replicated Slab

## Slide 66
Moment design
use as bottom steel in X-direction.
use as top steel in X-direction.
Shear design
ᴓVc>Vu

## Slide 67: Beam System

## Slide 68: Beam Detailing

## Slide 69: Column

## Slide 70: Column Detailing

## Slide 71: Column Detailing

## Slide 72: Shear Wall Design

## Slide 73: Shear Wall Design

## Slide 74: Footing & Tie Beam

## Slide 75: Footing

## Slide 76: Footings Reinforcement

## Slide 77: Footings Detailing

## Slide 78: Footings Detailing

## Slide 79: Footings Detailing

## Slide 80: Footings Detailing

## Slide 81: Wall Footings Detailing

## Slide 82: Tie beams desing

## Slide 83: Tie beams Detailing

## Slide 84: stair Detailing

## Slide 85: Design of water tank
Volume= 550 m3

## Slide 86: water tank Detailing

## Slide 87: Design beams of water tank

## Slide 88: water tank Detailing

## Slide 89: Chapter 4 : Electro-Mechanical This chapter of the project includes all the details and requirements related to the electrical and mechanical aspect; they are:

## Slide 90: 4.1 Artificial lighting design
Illuminance (lux)
Uniformity
Glare
artificial lighting design factor

## Slide 91: Types of luminaires
parking
storage rooms
Bathroom
rooms

## Slide 92: luminaires distribution
ground floor

## Slide 93
second floor
First floor

## Slide 94
basement floor

## Slide 95: 3D Views
Parents meeting room
kindergarten room

## Slide 96
library
parking
dining room

## Slide 97: power Design 4.2
Components of the electrical system
weirs
sockets
distrbution board
circuit breakers
load lighting and power

## Slide 98
distribution of the main and branch distribution boards
position of the main distribution boards (basement)

## Slide 99
The lighting power and electrical load Calculation
Basement
ground floor

## Slide 100
first floor

## Slide 101
The electrical load of elevators and HVAC

## Slide 102: 4.3Acoustic design
There are two considerations
Architectural side
Electro- acoustic side
The spaces that were designed acoustically in the faculty
Classroom
Multipurpose hall
Art \ music room

## Slide 103: Multipurpose hall

## Slide 105: Art/ music room

## Slide 106: Classroom

## Slide 107: 4.4 Fire alarm and Firefighting systems
Evacuation ways:
Evacuation routes on the first floor
Evacuation routes on the first floor

## Slide 108: Fire alarm systems

## Slide 109
distribution of Fire Hose Cabinet (ground floor)

## Slide 110
sprinklers system:
The selection of sprinkler

## Slide 112: 4.5 Water supply
Ground floor
first floor

## Slide 113: 4.6 Drainage system
Ground floor
first floor

## Slide 114: 4.7storm water tank
Rainwater plane for the roofs of school

## Slide 115: 4.8 Vertical transportation
Elevator selection

## Slide 116
PV system & HVAC system
PV system used
PV system simulation – pv sys & rescreen
PV system cash flow
HVAC system used
HVAC system steps in calculating

## Slide 117
Photovoltaics system

## Slide 118
1.1 Pv system used
We used a pv panels on the building roof.
79 photovoltaics panel shall be used, each on produce 345 wp
Monocrystalline silicon with 24% cell efficiency and 14-17.5 % module efficiency
Dimension: (L=1.95 m, W=0.95 m, D=0.04m)
By Landscape – distribution way we need 79 panel, by Portrait we need 68 panel.
Orientation: South with fixation angle of 35 degree (as winter semester needed angle)
The goal is not producing the maximum, it’s how to selected the orient and fixation angle that will produce energy during all the solar hour-year.

## Slide 119
79 panel each one produces 345 wp, all of them= 27.26 kwp
Assume that every day there is 8 hours’ solar radiation gain from sun in Jordan
27.26 kwp * 8 hr = 218.04 kwp/day
218.04 kwp/day * 365 day = 79,584.6 kwp
Assume that 20% dropped: from the year – the sky will be partially/totally clouded and fro the inverter efficiency and maintenance
79,584.6 kwp * 80 % = 63,667.68 kwp / yearly

## Slide 120
1.2 Pv system- pv sys. and Rest screen
Pv sys
Produced Energy 58.89 MWh/year
Performance ratio 74%

## Slide 121
Ret Screen

## Slide 122
Ret Screen – Financial visibility

## Slide 123
HVAC system

## Slide 124
HVAC VRF system,
The following information have been collecting from Design Builder simulation summary:
Relative humidity is between (30-50) %
21° in winter and 24° in summer
Total cooling capacity = 130.36 kw
Total heating capacity = 75.13 kw
Using these steps:
Design capacity, total load and volumetric flow rate
Diffusers needed for each space
Fresh air
Fan coil unit
Ducted sizes

## Slide 125
 | Zone | Design Capacity (kW) | Heating load (W/m2) | Total heating load (KW) | Mass Flow rate (Kg/s) | Volume Flow rate (m3/s)
G.F | Entrance | 2.02 | 39.840 | 62.646 | 0.25 | 0.205
G.F | Kg-3 | 2.21 | 45.059 | 70.851 | 0.27 | 0.224
G.F | Library | 1.83 | 39.933 | 62.792 | 0.22 | 0.186
G.F | Corridor 2 | 1.5 | 23.374 | 36.754 | 0.18 | 0.152
G.F | Multipurpose room | 4.41 | 55.772 | 87.697 | 0.54 | 0.447
G.F | Dining room | 6.61 | 102.513 | 161.193 | 0.81 | 0.671
G.F | Secretary room | 0.7 | 34.965 | 54.979 | 0.09 | 0.071
G.F | Food preparation | 0.93 | 30.760 | 48.368 | 0.11 | 0.094
G.F | Wc's | 0.62 | 27.249 | 42.847 | 0.08 | 0.063
G.F | Art room | 1.64 | 29.023 | 45.636 | 0.20 | 0.166
G.F | Kg-2 | 1.76 | 36.746 | 57.780 | 0.21 | 0.179
G.F | Kg-1 | 2.28 | 52.688 | 82.847 | 0.28 | 0.231
G.F | Wc's 1 | 0.48 | 16.076 | 25.278 | 0.06 | 0.049
G.F | Accountant room | 0.81 | 32.964 | 51.833 | 0.10 | 0.082
G.F | Regrestration | 0.77 | 34.588 | 54.387 | 0.09 | 0.078
G.F | Manger room | 1.13 | 45.697 | 71.855 | 0.14 | 0.115
G.F | Lobby | 3.82 | 63.333 | 99.587 | 0.47 | 0.388
G.F | Parents meeting room | 1.26 | 57.399 | 90.255 | 0.15 | 0.128
Design capacity, total load and volumetric flow rate

## Slide 126
Diffusers needed for each space
 | Zone | Design Flow rate m3/s | Space Flow rate m3/s | # diffuser | # diffuser
G.F | Entrance | 0.167 | 0.205 | 1.23 | 2.00
G.F | Corridor 2 | 0.167 | 0.152 | 0.91 | 1.00
G.F | Lobby | 0.189 | 0.388 | 2.05 | 2.00
G.F | Library | 0.150 | 0.186 | 1.24 | 2.00
G.F | Multipurpose room | 0.306 | 0.447 | 1.46 | 2.00
G.F | Dining room | 0.333 | 0.671 | 2.01 | 2.00
G.F | Parents meeting room | 0.136 | 0.128 | 0.94 | 1.00
G.F | Food preparation area | 0.147 | 0.094 | 0.64 | 1.00
G.F | Art room | 0.150 | 0.166 | 1.11 | 2.00
G.F | Kg-1 | 0.153 | 0.231 | 1.51 | 2.00
G.F | Kg-2 | 0.150 | 0.179 | 1.19 | 2.00
G.F | Kg-3 | 0.153 | 0.224 | 1.47 | 2.00
G.F | Wc | 0.142 | 0.049 | 0.35 | 1.00
G.F | Wc | 0.142 | 0.063 | 0.44 | 1.00
G.F | Secretary room | 0.142 | 0.071 | 0.50 | 1.00
G.F | Accountant room | 0.142 | 0.082 | 0.58 | 1.00
G.F | Regrestration | 0.142 | 0.078 | 0.55 | 1.00
G.F | Manger room | 0.142 | 0.115 | 0.81 | 1.00

## Slide 127
Fresh air
 | Zone | Fresh air/person(L/s) | #of students | Fresh air/person(L/s)
G.F | Library | 5.000 | 30.000 | 150.000
G.F | Multipurpose room | 5.000 | 40.000 | 200.000
G.F | Dining room | 5.000 | 40.000 | 200.000
G.F | Parents meeting room | 8.000 | 20.000 | 160.000
G.F | Food preparation area | 8.000 | 2.000 | 16.000
G.F | Art room | 5.000 | 20.000 | 100.000
G.F | Kg-1 | 5.000 | 25.000 | 125.000
G.F | Kg-2 | 5.000 | 25.000 | 125.000
G.F | Kg-3 | 5.000 | 25.000 | 125.000
G.F | Wc | 5.000 | 6.000 | 30.000
G.F | Wc | 8.000 | 6.000 | 48.000
G.F | Secretary room | 8.000 | 1.000 | 8.000
G.F | Accountant room | 8.000 | 1.000 | 8.000
G.F | Regrestration | 8.000 | 1.000 | 8.000
G.F | Manger room | 8.000 | 1.000 | 8.000

## Slide 128
Fan coil unit
 | Zone | Design Flow rate m3/s | Space Flow rate m3/s | #Fan coil unit | #Fan coil unit
G.F | Entrance | 0.185 | 0.205 | 1.11 | 1.00
G.F | Corridor 2 | 0.185 | 0.152 | 0.82 | 1.00
G.F | Lobby | 0.185 | 0.388 | 2.10 | 2.00
G.F | Library | 0.185 | 0.186 | 1.01 | 1.00
G.F | Multipurpose room | 0.185 | 0.447 | 2.42 | 3.00
G.F | Dining room | 0.185 | 0.671 | 3.63 | 4.00
G.F | Parents meeting room | 0.185 | 0.128 | 0.69 | 1.00
G.F | Food preparation area | 0.185 | 0.094 | 0.51 | 1.00
G.F | Art room | 0.185 | 0.166 | 0.90 | 1.00
G.F | Kg-1 | 0.185 | 0.231 | 1.25 | 1.00
G.F | Kg-2 | 0.185 | 0.179 | 0.97 | 1.00
G.F | Kg-3 | 0.185 | 0.224 | 1.21 | 1.00
G.F | Wc | 0.185 | 0.049 | 0.27 | 1.00
G.F | Wc | 0.185 | 0.063 | 0.34 | 1.00
G.F | Secretary room | 0.185 | 0.071 | 0.38 | 1.00
G.F | Accountant room | 0.185 | 0.082 | 0.44 | 1.00
G.F | Regrestration | 0.185 | 0.078 | 0.42 | 1.00
G.F | Manger room | 0.185 | 0.115 | 0.62 | 1.00

## Slide 129
Ducted sizes
Duct | Volumetric flow rate (L/s) | ΔP/EL | Velocity (m/s) | Duct size (mm * mm) | D (mm)
Main | 726 | 0.61 | 5.3 | (400*1050) | 500
B1 | 475 | 0.61 | 4.11 | (450*1550) | 600
B1 | 200 | 0.61 | 2.89 | (270*1135) | 600
B3 | 235 | 0.61 | 2.89 | (270*1135) | 600