## Slide 1
Design of a Wastewater Collection Network for Kifl Hares Village along with cost estimate and assessment of potential location for a proposed Wastewater Treatment Plant
Prepared by
Ghada Emad Hammad
Rand Saleem Jadallah
Supervisor
Dr. Mohammad N. Almasri

## Slide 2: Outline
Introduction
Objectives
Study area
Methodology
Modeling and design
Results
Conclusions and Recommendations
Cost estimate of WWCN
The proposed location of WWTP

## Slide 4: Objectives
-Design a wastewater collection network for Kifl Hares Village using SewerCAD.
- Calculate the cost.
-Location of proposed Wastewater Treatment Plant.

## Slide 5: Study Area
Study Area
515 m
410 m
r= 3.3%
Chart: 
| 1997 | 2007 | 2017
 | 2354 | 3248 | 4054

## Slide 6
Methodology
Determine problem
Selection of study area
Data collection
Loads determination
Design Wastewater Collection Network
Calculate the cost of a network
Location of WWTP

## Slide 7
Data
AutoCAD
Village Council
Data collection
Population
word
PCBS
Communities
GIS
Dr
Settlements
GIS
Dr

## Slide 8: Network
278
278

## Slide 9
Load calculations

## Slide 10
Total Load = peak WW generation for the MH. + MH. Load of Infiltration
=Load of WW generation + 0.05 × load of WW generation
Load of WW generation = ((# of building × # of person/building) ×) × 0.11 × 0.8 × 4
Take manhole-1
= ((6 × 7) × ) × 0.11 × 0.8 × 4 = 33.28/d
= 33.28+0.05×33.28 = 34.94 /d
# of person/building = 7
Design period = 25
Growth rate =0.033
Water consumption=0.110
Load calculations

## Slide 12
Design constraints
Velocity
Cover
Slope
0.6-3m/s
1-5m
1-12%
Partial flow
80%

## Slide 13: Manholes and conduits information

## Slide 16
Before
After use Drop manholes

## Slide 17: Data profile
Ground surface
Total Energy Line
Hydraulic Grade Line

## Slide 18
Data profile

## Slide 19
Data profile

## Slide 20
Excavation
Manholes
Conduits
Re-paving
Others
Estimation of Potential Cost
Network Elements

## Slide 21
Excavation
117,763 $
calculated as.
width
length
depth
25cm+D+25cm
Distance between two manholes
Avg cover+D+20cm
1 m3 excavation for 8in conduit = 12 $.

## Slide 22
Conduits
98,046 $
Calculated in linear meter
1 m of 8in diameter PVC conduit = 13 $
Depends on:
Length
Dimeter
Material

## Slide 23
Manholes
MH element | Dimensions | Cost
Base | 100×60 | $99
 | 100×80 | $115
Cone | 100×75 | $99
Cover | 100×20 | $61
Ring | 100×30 | $54
 | 100×40 | $56
 | 100×50 | $57
50,018 $

## Slide 24
Re-paving
95,029 $
Cost of 1 =18 $.
length
width
Length of the network =7542 m
0.7 m

## Slide 25
Other cost
Labor
Insurance
Transportation
Engineer salary
Installing manholes
108,820 $

## Slide 26
Cost percentage of Network Elements ($)
Chart: 
| Excavation | Conduits | Manholes | Re-paving | Others
 | 25.0732 | 20.8752 | 10.6495 | 20.2329 | 23.1692

## Slide 27
Item | Cost ($) | Percentage (%)
Excavation | 117,763 | 25%
Conduits | 98,046 | 21%
Manholes | 50,018 | 11%
Asphalt | 95,029 | 20%
Others | 108,820 | 23%
Total cost | 469,676 | 100%
Cost/m | 62 | -
Cost/person | 52 | -

## Slide 28
Proposed location for potential Wastewater Treatment Plant

## Slide 29
Selection criteria for the WWTP location.
15
14
13
11
12
8
10
9
7
6
5
2
4
3
Geopolitical area
Population served.
Remoteness from residential areas.
The zones to be served.
Prevailing wind directions.
The public opinion.
Access by an existing road.
Type of the soil.
Land acquisition.
Topography.
The susceptibility of the site to flooding.
Traffic and dust pollution.
Remoteness from areas recharge of the Groundwater.
Geotechnical stability.
1
Noise and lighting

## Slide 31
Distribution of the settlements in the area.

## Slide 36
Location | No. of served villages | Villages served | Existing population (capita) | Future population (capita) | Quantity of WW/d)
A | 6 | Marda, Iskaka, Yasuf ,Kifl Hares, Qira and Jamma’in | 18,373 | 34,903 | 9,214
B | 7 | Marda, Iskaka, Yasuf, Kifl hares, Qira, Jamma’in and Zeta | 20,940 | 39,779 | 10,501
C | 16 | Marda, Iskaka, Yasuf, Kifl hares, Qira, Jamma’in, Zeta ,Deir Istiya, ’Urif , ’Asira al Qibliya, Huwwara ,Odala, ’Einabus, Madama, Burin and ’Awarta | 53,903 | 102,339 | 27,033
D | 19 | Marda, Iskaka, Yasuf, Kifl hares, Qira, Jamma’in, Zeta ,Deir Istiya, ’Urif , ’Asira al Qibliya, Huwwara ,Odala, ’Einabus, Madama, Burin, ’Awarta, Haris, Biddya and Qarawat Bani Hassan | 72,075 | 136,920 | 36,147
Location | No. of served villages | Villages served | Existing population (capita) | Future population (capita) | 
A | 6 | Marda, Iskaka, Yasuf ,Kifl Hares, Qira and Jamma’in | 18,373 | 34,903 | 9,214
B | 7 | Marda, Iskaka, Yasuf, Kifl hares, Qira, Jamma’in and Zeta | 20,940 | 39,779 | 10,501
C | 16 | Marda, Iskaka, Yasuf, Kifl hares, Qira, Jamma’in, Zeta ,Deir Istiya, ’Urif , ’Asira al Qibliya, Huwwara ,Odala, ’Einabus, Madama, Burin and ’Awarta | 53,903 | 102,339 | 27,033
D | 19 | Marda, Iskaka, Yasuf, Kifl hares, Qira, Jamma’in, Zeta ,Deir Istiya, ’Urif , ’Asira al Qibliya, Huwwara ,Odala, ’Einabus, Madama, Burin, ’Awarta, Haris, Biddya and Qarawat Bani Hassan | 72,075 | 136,920 | 36,147

## Slide 37
 | Weights (W) | Location A | Location B | Location C | Location D
Population served. | 14 | Bad | Good | Very good | Excellent
Remoteness from residential areas | 13 | Bad | Good | Very good | Very good
The zones to be served. | 12 | Excellent | Excellent | Excellent | Excellent
Access by an existing road | 9 | Excellent | Very good | Excellent | Very good
Remoteness from flooding zone | 5 | Very good | Very good | Very good | Very good
Land acquisition. | 7 | Bad | Bad | Bad | Bad
Noise and lighting | 1 | Excellent | Excellent | Excellent | Excellent
Traffic and dust pollution | 4 | Bad | Good | Bad | Good
Topography | 6 | Good | Bad | Bad | Bad
Geotechnical stability | 2 | Good | Good | Good | Good
Winds direction. | 11 | Good | Good | Good | Good
Geopolitical area | 15 | Good | Bad | Bad | Bad
Type of the soil | 8 | Bad | Good | Good | Good
Areas recharge of the ground water | 3 | Good | Good | Good | Good
The public opinion | 10 | Bad | Bad | Bad | Bad
Excellent = 10
Very good = 7
Good = 4
Bad = 2

## Slide 38
 | Weights )W) | Location A (W*M) | Location B (W*M) | Location C (W*M) | Location D (W*M)
Population served. | 14 | 28 | 56 | 98 | 140
Remoteness from residential areas | 13 | 26 | 52 | 91 | 91
The zones to be served. | 12 | 120 | 120 | 120 | 120
Access by an existing road | 9 | 90 | 63 | 90 | 63
Remoteness from flooding zone | 5 | 35 | 35 | 35 | 35
Land acquisition. | 7 | 14 | 14 | 14 | 14
Noise and lighting | 1 | 10 | 10 | 10 | 10
Traffic and dust pollution | 4 | 8 | 16 | 8 | 16
Topography | 6 | 24 | 12 | 12 | 12
Geotechnical stability | 2 | 8 | 8 | 8 | 8
Winds direction. | 11 | 44 | 44 | 44 | 44
Geopolitical area | 15 | 60 | 30 | 30 | 30
Type of the soil | 8 | 16 | 32 | 32 | 32
Areas recharge of the ground water | 3 | 12 | 12 | 12 | 12
The public opinion | 10 | 20 | 20 | 20 | 20
Sum | - | 483 | 492 | 592 | 615

## Slide 40
Conclusions
# of manholes | 278
# of conduits | 278
# of outfalls | 4
Diameters | 8 in
Cover depth | (1.20-6.84)m
Velocity | (0.6-2.67)m/s
Slope | (1-12)%
Cost/m | 62 $/m
Cost/person | 52 $/person