## Slide 1
An-Najah University
Energy And Environmental Engineering
Graduation Project 2
Nablus Western WWTP Sludge Management Development – Techno – economic Approach
Prepared by:
Esraa Zammar
Mai Saboobah
Supervised by:
Dr. Abd Elrahim Abusafa
Dr. Mohammad Alsayed

## Slide 2
02
01
INTRODUCTION
Global Wastewater Challenge: Ineffective wastewater management leads to pollution and health risks, with 45 million dry tons of sludge generated annually worldwide, requiring significant investment in infrastructure.
45 million dry tons generated annually worldwide.
03
Palestinian Context: 46.1% of the West Bank and 16.4% of Gaza lack sewage net45 million dry tons generated annually worldwide. Works, causing severe environmental and health risks.
45 million dry tons generated annually worldwide.
04
Need for Effective Sludge Treatment: Developing effective methods for sludge treatment is crucial for environmental and economic sustainability.

## Slide 3
BACKGROUND
The sewage treatment plant is situated to the west of Nablus, approximately 12 kilometers from the city itself, within the territory of the town of Deir Sharaf.
In 2022

## Slide 4
PROBLEM STATEMENT
2. Project Goals: Evaluate "greenhouse solar drying" vs. current methods, focusing on environmental, health, and economic impacts to improve sustainable sludge management.
1.Current Challenges: Western Nablus WWTP struggles with sludge management, needing to dry sludge from 26% to 90% dry solid content for fertilizer or 50% for soil conditioner to reduce landfill strain

## Slide 5
OBJECTIVE
01
02
03
02
03
Evaluate Current System: Assess the Western Nablus WWTP's sludge drying for environmental and health compliance.
Solar Drying Potential: Explore using greenhouse solar drying to achieve 90% dry solids, considering environmental and economic impacts.
Feasibility Design: Plan and design greenhouse solar drying for Western Nablus WWTP, ensuring compliance with Palestinian standards and conducting cost-benefit analysis.

## Slide 6
Information Gathering
Selection of the Optimal Method
Economic Feasibility Assessment
Impact Assessment
METHODOLOGY
Greenhouse Design
Recommendations

## Slide 7
Selection of the Optimal Method
Economic Feasibility Assessment
Process Design
Impact Assessment
METHODOLOGY
OPTION ANALYSIS
PYROLOSIS
COMPOSTING
N
INCINERATION
SOLAR DRYING
GASIFICATIN

## Slide 8
SOLAR DRYING
Greenhouse
Solar bed

## Slide 9
DESIGN GREENHOUSE
SOLAR DRYER

## Slide 10
Study Area and Environmental Conditions
Months | Outdoor Temperature |  |  | Relative Humidity (%) | Solar Radiation(W/m2) | air density (Kg/m3)
 | Ta_MAX | Ta_MIN | Ta_AVG |  |  | 
January | 16.58 | 9.32 | 12.95 | 75.54 | 122.92 | 1.31
February | 16.92 | 10.15 | 13.53 | 77.25 | 132.71 | 
March | 18.03 | 10.66 | 14.34 | 80.22 | 168.72 | 
April | 21.34 | 12.08 | 16.71 | 71.22 | 245.00 | 
May | 28.38 | 16.75 | 22.56 | 60.14 | 312.16 | 
June | 30.43 | 21.26 | 25.84 | 64.49 | 329.06 | 
July | 32.18 | 22.78 | 27.48 | 63.34 | 345.27 | 
August | 32.62 | 23.86 | 28.24 | 65.95 | 313.52 | 
September | 31.18 | 22.64 | 26.91 | 68.23 | 260.99 | 
October | 29.30 | 20.69 | 25.00 | 67.34 | 190.24 | 
November | 26.47 | 15.93 | 21.20 | 52.8 | 153.50 | 
December | 19.42 | 11.99 | 15.70 | 71.85 | 100.54 | 
Months |  |  |  | Relative Humidity (%) | Solar Radiation(W/m2) | air density (Kg/m3)
 | Ta_MAX | Ta_MIN | Ta_AVG |  |  | 
January | 16.58 | 9.32 | 12.95 | 75.54 | 122.92 | 1.31
February | 16.92 | 10.15 | 13.53 | 77.25 | 132.71 | 
March | 18.03 | 10.66 | 14.34 | 80.22 | 168.72 | 
April | 21.34 | 12.08 | 16.71 | 71.22 | 245.00 | 
May | 28.38 | 16.75 | 22.56 | 60.14 | 312.16 | 
June | 30.43 | 21.26 | 25.84 | 64.49 | 329.06 | 
July | 32.18 | 22.78 | 27.48 | 63.34 | 345.27 | 
August | 32.62 | 23.86 | 28.24 | 65.95 | 313.52 | 
September | 31.18 | 22.64 | 26.91 | 68.23 | 260.99 | 
October | 29.30 | 20.69 | 25.00 | 67.34 | 190.24 | 
November | 26.47 | 15.93 | 21.20 | 52.8 | 153.50 | 
December | 19.42 | 11.99 | 15.70 | 71.85 | 100.54 | 
Meteorological data

## Slide 11
Calculations of Evaporation rate
Month | Outdoor Temp | Outdoor Solar Radiation(W/m2) | Evaporation Rate (Kg/m2. h) | Evaporation Rate (Kg/m2. d) | Air Density Kg/m3
January | 12.95 | 122.92 | 0.2708 | 6.4679 | 1.31
February | 13.53 | 132.71 | 0.2849 | 6.9033 | 
March | 14.34 | 168.72 | 0.3220 | 7.7022 | 
April | 16.71 | 245.0 | 0.4220 | 9.9106 | 
May | 22.56 | 312.16 | 0.6019 | 14.3111 | 
June | 25.84 | 329.06 | 0.6957 | 16.6687 | 
July | 27.48 | 345.27 | 0.7561 | 18.1249 | 
August | 28.24 | 313.52 | 0.7314 | 17.5966 | 
September | 26.91 | 260.99 | 0.6339 | 15.3055 | 
October | 25.0 | 190.24 | 0.5157 | 12.4872 | 
November | 21.20 | 153.50 | 0.4127 | 9.9768 | 
December | 15.70 | 100.54 | 0.2926 | 7.0869 | 
Month |  | Outdoor Solar Radiation(W/m2) | Evaporation Rate (Kg/m2. h) | Evaporation Rate (Kg/m2. d) | Air Density Kg/m3
January | 12.95 | 122.92 | 0.2708 | 6.4679 | 1.31
February | 13.53 | 132.71 | 0.2849 | 6.9033 | 
March | 14.34 | 168.72 | 0.3220 | 7.7022 | 
April | 16.71 | 245.0 | 0.4220 | 9.9106 | 
May | 22.56 | 312.16 | 0.6019 | 14.3111 | 
June | 25.84 | 329.06 | 0.6957 | 16.6687 | 
July | 27.48 | 345.27 | 0.7561 | 18.1249 | 
August | 28.24 | 313.52 | 0.7314 | 17.5966 | 
September | 26.91 | 260.99 | 0.6339 | 15.3055 | 
October | 25.0 | 190.24 | 0.5157 | 12.4872 | 
November | 21.20 | 153.50 | 0.4127 | 9.9768 | 
December | 15.70 | 100.54 | 0.2926 | 7.0869 | 

## Slide 12
Month | 19.JAN | 18.JUL
Evaporation Rate(Kg/m2.h) | 0.1831 | 1.7936
Calculations of Evaporation rate

## Slide 13
Calculations of Evaporation rate
Chart: Evaporation Rate(Kg/m2.h)
| January | February | March | April | May | June | July | August | September | October | November | December
Evaporation Rate(Kg/m2.h) | 0.27083 | 0.28486 | 0.32203 | 0.42204 | 0.60194 | 0.6957 | 0.75609 | 0.73145 | 0.6339 | 0.5157 | 0.41274 | 0.29264
Evaporation Rate(Kg/m2.d) | 6.4679 | 6.9033 | 7.7022 | 9.9106 | 14.3111 | 16.6687 | 18.1249 | 17.5966 | 15.3055 | 12.4872 | 9.9768 | 7.0869

## Slide 14
VENTELATION RATE
Qv(m3/m2.h) | Evaporation Rate (Kg/m2.h)
130 | 0.1831
120 | 0.1770
100 | 0.1639
80 | 0.1491
50 | 0.1222
20 | 0.0830
Chart: Qv(m3/m2.h)
| 130 | 120 | 100 | 80 | 50 | 20
 | 0.1831 | 0.177 | 0.16386 | 0.1491 | 0.12222 | 0.082951

## Slide 15
AIR MIXING RATE
In our study, we used a Qm of 90 m3/m2·h, achieved by installing 30 units with an air mixing rate of 2.9623 m3/m2·h. This configuration effectively maintained the desired air mixing without notable impact on the evaporation rate.

## Slide 16
FANS AND EXHAUST FANS
Category | Solar-Powered Fans | Exhaust Fans
Quantity | 30 fans | 37 fans
Power | 25 watts per fan | 250 watts per fan
CFM | 360 CFM | 4900 CFM

## Slide 17
CALCULATIONS OF GREENHOUSE AREA
Month | Evaporation Rate (Kg/m2.h) | Daily Sludge mass(t/d) | σ (kg[solids]/ kg[sludge]) | final DS achieved (%) | Area (m2) | construction cost of GSD (ILS)
January | 0.2708 | 15 | 0.28 | 90 | 1801 | 72047.7
February | 0.2849 |  |  |  | 1729 | 69165.8
March | 0.3220 |  |  |  | 1605 | 64211.3
April | 0.4220 |  |  |  | 1340 | 53603.3
May | 0.6019 |  |  |  | 991 | 39659.5
June | 0.6957 |  |  |  | 862 | 34468.1
July | 0.7561 |  |  |  | 806 | 32244.6
August | 0.7314 |  |  |  | 813 | 32512.7
September | 0.6339 |  |  |  | 893 | 35714.3
October | 0.5157 |  |  |  | 1026 | 41037.2
November | 0.4127 |  |  |  | 1225 | 49010.1
December | 0.2926 |  |  |  | 1624 | 64966.5

## Slide 18
CALCULATIONS OF GREENHOUSE AREA
Chart: 
Area (m2) | 1801.1928 | 1729.1438 | 1605.2821 | 1340.0831 | 991.4876 | 861.7036 | 806.1138 | 812.8172 | 892.8586 | 1025.9306 | 1225.2519 | 1624.1613
construction cost of GSD i | 72047.7118 | 69165.7516 | 64211.2824 | 53603.3242 | 39659.5021 | 34468.1444 | 32244.55 | 32512.6887 | 35714.3426 | 41037.2234 | 49010.0749 | 64966.4505
Chart: Evaporation Rate(Kg/m2.h)
| January | February | March | April | May | June | July | August | September | October | November | December
Evaporation Rate(Kg/m2.h) | 0.27083 | 0.28486 | 0.32203 | 0.42204 | 0.60194 | 0.6957 | 0.75609 | 0.73145 | 0.6339 | 0.5157 | 0.41274 | 0.29264
Area (m2) | 1801.1928 | 1729.1438 | 1605.2821 | 1340.0831 | 991.4876 | 861.7036 | 806.1138 | 812.8172 | 892.8586 | 1025.9306 | 1225.2519 | 1624.1613

## Slide 19
CONSTRUCTION COSTS FOR GSD INSTALLATION AND EQUIPMENT
construction cost of GSD (ILS) | 94,060.4
CO2 sensor (ILS) | 1,015.2
temp&humidity sensor (ILS) | 818.9
30 FAN 360CFM (ILS) | 10,152.0
37 exhaust fan (ILS) | 116,548.7
Total (ILS) | 187,258.6

## Slide 20
SLUDGE TRANSPORTATION COSTS TO ZAHRET AL-FINJAN LANDFILL
After Drying
Before Drying
120.00 | ILS/ton
15.00 | ton /day
33.48 | Gate fees (ILS/ton)
2,302.20 | ILS/day
840,303.00 | per year
64,461.60 | per month
120.00 | ILS/ton
4.70 | ton /day
33.48 | Gate fees (ILS/ton)
721.36 | ILS/day
263,294.94 | per year
20,197.97 | per month

## Slide 21
RECOMMENDATION
Cost (ILS) | 5,264
fixed cost for year (ILS) | 47,304
fixed cost per month (ILS) | 3888
cost (ILS) | 33,539
fixed cost for year (ILS) | 488,370
fixed cost per month (ILS) | 40,140
LIGHTING
LIGHTING FOR HEATING

## Slide 22
RECOMMENDATION
ELECTRIC MOLE

## Slide 23
CONCLUSION
The greenhouse solar dryer at Nablus West Purification Station is a highly effective and economically prudent solution for sludge treatment. By drying 15 tons of sludge to 90% dry solids, reducing its moisture content to 4,700 tons, and achieving a remarkable ROI of 282.17% with a short SPP of 0.354 years, it significantly cuts transportation costs. This approach not only optimizes logistical efficiency but also underscores the dryer's cost-effectiveness and quick recoupment of initial investment.

## Slide 24
THANK YOU