## Slide 1
An-Najah National University
Faculty of Engineering & Information Technology
Building Engineering Department
Group members:
Adnan Arafat
Mohy Darwazeh
Khalil Tanbour
Supervisor name: Eng.Hasan Mathar
Graduation Project 1
“Holy Qur’an Academy Primary School “

## Slide 2: Table of Content :
1
2
3
4
Introduction
Environmental-Architectural Aspects
Structural Aspects
Electro-Mechanical Aspects
5
Quantity Surveying and Cost Estimate

## Slide 3
Introduction:
The school building is one of the most important basics of the educational process, and the most important factor for success is the educational process.
Studies have shown that the more the school building is equipped with amenities, the greater the educational attainment of students and helps in the proper functioning of the educational process. So the study environment is the place where students receive pedagogical and educational principles and take them to society to develop and build it.

## Slide 4
Site Analysis:
Location: It is located in the west north of Nablus city with near of Asira Al-Shamalya village.
Site area: 15030.88 SM.

## Slide 5
Environmental-Architectural Aspects :

## Slide 6
4 Floors including two basements and two floors.
Serve 550 student.
Total area of the building equals to 3411.22 SM
Architectural Aspects :
Project description:

## Slide 7
Project Plans:
Site Plan:
Architectural Aspects :

## Slide 8
Project Floor Plans:
B2 floor Plan
B1 floor Plan
Architectural Aspects :

## Slide 9
Project Floor Plans:
Ground floor Plan
First floor Plan
Architectural Aspects :

## Slide 10
Project Elevations:
Western elevation
Architectural Aspects :

## Slide 11
Project Elevations:
Architectural Aspects :

## Slide 12
Project Elevations:
Architectural Aspects :

## Slide 13
Project Elevations:
Architectural Aspects :

## Slide 14
Project sections:
Architectural Aspects :

## Slide 15
Project sections:
Architectural Aspects :

## Slide 16
Sun Path:
Depending on Palestine location so the sun path is wide in summer and narrow in winter with Altitude in summer (21-6) is 81.5 and in winter (21-12) is 34.7 .
Sun path – Winter condition
Sun path – Summer condition
Architectural Aspects :

## Slide 17
B2 floor Plan
B1 floor Plan
Sun Path on floors:
Architectural Aspects :

## Slide 18
Sun Path on floors:
Ground floor Plan
First floor Plan
Architectural Aspects :

## Slide 19
B2 floor Plan
B1 floor Plan
View analysis on floors:
Architectural Aspects :

## Slide 20
View analysis on floors:
Ground floor Plan
First floor Plan
Architectural Aspects :

## Slide 21
B2 floor Plan
B1 floor Plan
Wind analysis on floors:
Architectural Aspects :

## Slide 22
Wind analysis on floors:
Ground floor Plan
First floor Plan
Architectural Aspects :

## Slide 23
B2 floor Plan
B1 floor Plan
Noise analysis on floors:
Architectural Aspects :

## Slide 24
Noise analysis on floors:
Ground floor Plan
First floor Plan
Architectural Aspects :

## Slide 25
Architectural Aspects :
Function | Actuel Area (m2) | Standard area (m2) |  | Check
Administrative |  |  |  | 
Principle office | 24.5 | 20-30 | ok | 
Secretary | 14.5 | 20-24 | Not ok | 
meeting room | 39.17 | 80-85 | Not ok | 
social guidance | 26 | 20 | ok | 
Services |  |  |  | 
First Aid | 16.5 | 20 | ok | 
Reception | 82.5 | 25 | ok | 
Multipurpose hall | 89.21 | 90 | ok | 
Canteen | 21.19 | 40-60 | Not ok | 
Kitchens | 23.5 | *** | ok | 
Staff W.Cs | 31.9 | 15 | ok | 
Store | 17.9 | *** | ok | 
*Student W.Cs | 84.225 | *** | Not ok | 
Educational Spaces |  |  |  | 
Classroom 1 | 39.36 | 45 | Not ok | 
Classroom 2 | 35.88 | 45 | Not ok | 
Classroom 3 | 42.1 | 45 | ok | 
Classroom 4 | 42.21 | 45 | ok | 
Classroom 5 | 48.45 | 45 | ok | 
Classroom 6 | 46.6 | 45 | ok | 
Classroom 7 | 46.1 | 45 | ok | 
Classroom 8 | 51.78 | 45 | ok | 
Classroom 9 | 45.82 | 45 | ok | 
Function | Actuel Area (m2) | Standard Area (m2) | Check
Classroom 11 | 44.6 | 45 | ok
Classroom 12 | 38.2 | 45 | Not ok
Classroom 13 | 39.8 | 45 | Not ok
Classroom 14 | 46.1 | 45 | ok
Classroom 15 | 46.25 | 45 | ok
Classroom 16 | 48.2 | 45 | ok
Classroom 17 | 47.3 | 45 | ok
Classroom 18 | 45.82 | 45 | ok
Classroom 19 | 45.8 | 45 | ok
Classroom 20 | 49.1 | 45 | ok
Classroom 21 | 45 | 45 | ok
Classroom 22 | 45.23 | 45 | ok
Classroom 23 | 45.23 | 45 | ok
**Library | 106.16 | 50-70 | Not ok
Science lab | 51.75 | 70-80 | Not ok
Computer lab | 46.6 | 40.5 | ok
Teacher's rooms | 89.22 | 24-50 | ok
Circulation |  |  | 
Staircase A | 24.55 | *** | ok
Staircase B | 23.8 | *** | ok
Modifications:
Area modification:

## Slide 26
Modifications:
Room orientation:
The original location of computer lab
The modified location of computer lab
Architectural Aspects :

## Slide 27
Modifications:
Room orientation:
The original location of the library
The modified location of the library
Architectural Aspects :

## Slide 28
Modifications:
Glazing Area:
The area of glazing in each classroom should be 20% of classroom area, so the glazing area modified to achieve this requirement.
Glazing area before modification
Glazing area after modification
Architectural Aspects :

## Slide 29
Modifications:
Green Area:
The modified court
Court before modification - As-built
Architectural Aspects :

## Slide 30
Modifications:
Safety Modifications:
Science lab is located in the first floor so it moved to second basement to make it near to exits in case any hazard occurred.
The original location of science lab
The modified location of science lab
Architectural Aspects :

## Slide 31
Modifications:
stair case A modified to work as an emergency staircase by adding insulation to its walls and make emergency doors in each floor.
Safety Modifications:
Architectural Aspects :

## Slide 32
Environmental Aspects :

## Slide 33
Design Builder Modeling:
Environmental Aspects :

## Slide 34
HVAC System ( Heating and Cooling )
Construction Layers for External Layers:
Environmental Aspects :
Wall Layers and U-Value before modification
Wall Layers and U-Value after modification
Some modifications were made to the main layers that formed the external walls and adding some types of insulation materials with certain thicknesses to make the wall energy efficient and to decrease the amount of thermal conductivity.
The U-value is equal 0.287 (W/m2.K) which is less than 0.5 (W/m2.K) so the U-value is efficient.

## Slide 35
HVAC System ( Heating and Cooling )
Environmental Aspects :
Flat Roof Layers and U-Value before modification
Flat Roof Layers and U-Value after modification
Some modifications were made to the main layers that formed the flat roof and adding some types of insulation materials with certain thicknesses to make the flat roof energy efficient and to decrease the amount of thermal conductivity.
As shown on the figure above, the U-value is equal 0.354 (W/m2.K) which is less than 0.4 (W/m2.K) so the U-value is efficient.
Construction Layers for Flat Roof Layers:

## Slide 36
HVAC System ( Heating and Cooling )
Environmental Aspects :
Layers for Glazing Area and Windows :
Glazing Layers and U-Value before modification
Glazing Layers and U-Value before modification
Some modifications were made to the main layers that formed the glazing area and adding more layers to make the glazing area and window energy efficient and to decrease the amount of thermal conductivity.

## Slide 37
HVAC System ( Heating and Cooling )
Environmental Aspects :
Lighting System :
Lighting system has an impact on heating and cooling values by the amount of radiant heat which affected by lamp type, luminaire fixation, power density and control system.
To reduce the values of heating and cooling, the type of lamp used is LED with linear control, this type increases the efficiency and reduce the energy consumption.
Lighting system before modification
Lighting system after modification

## Slide 38
Environmental Aspects :
HVAC System ( Heating and Cooling )
Shading System:
Shading system affect the amount of solar insolation fallen on spaces, so the heating and cooling load values will change according to shading system design so two techniques used in the building as shown below:
Polycarbonate coverage for the court.
Alcubond cantilever around all sides of the windows, it used to achieve architectural and environmental purposes
Polycarbonate Coverage for court
Alcubond cantilever around windows

## Slide 39
Chart: 
| 105.10999999999999
Cooling Load before | 259.93
Cooling Load after | 105.11
Heating Load Before | 221.65
Heating Load after | 64.94
Environmental Aspects :
HVAC System ( Heating and Cooling )
Depending on modifications and shading systems, a comparison between heating and cooling load before and after modification as shown in the tables below:

## Slide 40
Environmental Aspects :
CFD Analysis:
External CFD Analysis
CFD analysis for court
External CFD Analysis:

## Slide 41
Environmental Aspects :
CFD Analysis:
Internal CFD Analysis:
Internal CFD analysis in B2
Internal CFD analysis in B1

## Slide 42
Environmental Aspects :
CFD Analysis:
Internal CFD Analysis:
Internal CFD analysis in GF
Internal CFD analysis in FF

## Slide 43
Environmental Aspects :
Simulation Results:
After heating and cooling design and all modifications on construction, lighting and HVAC system, a comparison between simulation results before and after modifications as shown :
Energy Per Building Area (kWh/m2) before modification
Energy Per Building Area (kWh/m2) after modification

## Slide 44
Environmental Aspects :
Simulation Results:
The total uncomfortable hours before modification from 1-Jan to 31-Dec is = 1082 hrs.
The total uncomfortable hours after modification from 1-Jan to 31-Dec is = 644 hrs, it noticed that a large drop in total uncomfortable hours because multiple modifications were done on the building.
Total uncomfortable hours before modification
Total uncomfortable hours after modification

## Slide 45
Environmental Aspects :
Simulation Results:
PMV Analysis:
PMV is a predict mean value of votes to get an indication of the occupancy satisfaction about thermal feeling, the value of PMV should be between -0.5 to 0.5 as shown in the figure:

## Slide 46
Environmental Aspects :
Overshadowing analysis:
This analysis done in two specific times at 9:00 am and 12:00 pm for both summer (21-June) and winter (21-Dec) to study the effect of surrounding building and the building itself in terms of entrances and playground.
overshadowing analysis before modifications - 9:00 am - winter case
overshadowing analysis before modifications - 9:00 am - summer case

## Slide 47
Environmental Aspects :
Overshadowing analysis:
overshadowing analysis before modifications – 12:00 pm- winter case
overshadowing analysis before modifications - 12:00 pm- summer case

## Slide 48
Environmental Aspects :
Overshadowing analysis:
overshadowing analysis after modifications - 9:00 am - winter case
overshadowing analysis after modifications - 9:00 am - summer case

## Slide 49
Environmental Aspects :
Overshadowing analysis:
overshadowing analysis after modifications – 12:00 pm- winter case
overshadowing analysis after modifications - 12:00 pm- summer case

## Slide 50
Environmental Aspects :
Daylight Factor:
In this section daylight factor analysis has done on all the year ( 1/Jan to 31/ Dec ) to study how much of natural daylight enter to spaces through glazing area so it minimize the consumption of electricity and it also make occupancy feel comfortable in spaces.
Changing eastern entrance to glazing :
Court is located in the middle of the school and it should enter much natural light to illuminate the corridors and open areas ,so to improve it the eastern entrance modified to a glazing area so it allow to get more amount of natural light.

## Slide 51
Environmental Aspects :
Daylight for Ground floor - After modification
Daylight on Ground floor - Before modification
Daylight Factor:

## Slide 52
Environmental Aspects :
Daylight Factor:
By enlarging windows area, the amount of daylight will increase effectively and light up large area unlike small glazing area, so the modification was to make bigger windows with shading frame to increase lighting and decrease solar radiation.
Enlarge windows:

## Slide 53
Environmental Aspects :
Daylight Factor:
Enlarge windows:
Daylight for First floor - After modification
Daylight for First floor - Before modification

## Slide 54
Environmental Aspects :
Daylight Factor:
On the other hand, floors underground such as first and second floors are not exposed to direct sun so the amount is few and negligible so artificial light is vital in these floors to illuminate corridors and confined areas

## Slide 55
.
the structural design system used for this School building is a two way ribbed slab system, And Isolated footing
Structural aspects

## Slide 56
This structural design is done by using the following codes:
- ACI 318-11 for reinforced concrete structural design
-ASCE 7 2010 for load combinations
- UBC – 97 for earthquake design
Structural aspects

## Slide 57
Design data:
Concrete strength for all structural member f’c=28 mpa.
Steel yield strength fy=420 mpa.
Bearing capacity for soil = 400kN/m2
Structural aspects

## Slide 58
Loads
Structural aspects
Gravity loads
Live Loads
Superimposed loads
Dead loads
Lateral loads

## Slide 59
Live Loads:
School | Load (KN/N) | Concentrated load (KN)
Class room | 1.92 | 4.45
Corridor above first floor | 3.83 | 4.45
First floor corridors | 4.79 | 4.45
Table 4 : Structural loads
Structural aspects

## Slide 60
Lateral loads:
The city of structure is Nablus.
The seismic zone factor. Z=0.2.
The soil profile is type SD.
The acceleration seismic coefficient Ca=0.2
The velocity seismic coefficient Cv=0.2
The Seismic importance factor is 1.
The structural design type is intermediate, R=5.5
Structural aspects

## Slide 61
Structural aspects
Materials
Reinforced concrete
Property | Value
Compressive strength, fc ( MPa ) | 24
Modulus of elasticity, Ec ( GPa ) | 23
Unit weight (kN/m3 ) | 25
Steel reinforcement
Property | Value
Yielding strength, fy ( MPa ) | 420
Modulus of elasticity, Es ( GPa ) | 200

## Slide 62
Non – structural elements
Structural aspects
Materials
Material | Ɣ in kN/m³
Blocks | 12
Filling Materials | 18
Tiles | 26
Plaster | 23
Aggregate | 13
Concrete Mortar | 23
Masonry Stone | 30

## Slide 63
Structural aspects
Column distributed for Basement 2 and Basement 1

## Slide 64
Structural aspects
Column distributed for Ground floor

## Slide 65
Structural aspects
Column distributed for First floor

## Slide 66
Structural aspects
Beams distributed for Basement 2

## Slide 67
Structural aspects
Beams distributed for Basement 1

## Slide 68
Structural aspects
Beams distributed for Ground floor

## Slide 69
Structural aspects
Beams distributed for First floor

## Slide 70
Project modeling
1. Bring the layout of the project from AutoCAD architectural drawing.
2. Define the materials used in the building (concrete and steel).
3. Define element sections of the structure with their suitable modifiers.
4. Define area section (slabs and shear walls) with their suitable modifiers.
5. Define load patterns on the structure, such as Dead, Superimposed and live loads.
6. Define load combinations according to the code for analysis and design.
7. Draw the structural elements (sections) and slabs (area sections).
8. Assign the loads ( except own weight -dead- ) on structural elements and slabs according to the values of superimposed , and live loads.
9. And then make the checks!!

## Slide 71
Stiffness modifiers
Slabs 0.35
Beams 0.35
Columns and shear wall 0.7
Structural aspects

## Slide 72
Structural aspects
ETABS Model Checks
Compatibility check
Equilibrium check
Stress strain check
Deflection check
Period check
Drift Check
Base shear check

## Slide 73
Structural aspects
Compatibility check
The whole structural elements move as one body

## Slide 74
Structural aspects
Equilibrium check
This check done for Dead, SID and Live load within difference less than 5 %.
Load | Hand calculation | ETABS | %Difference | < 5%
Live | 15729.15 | 15705.63 | 0.14% | OK!
SID | 18479.81 | 18446.59 | 0.18% | OK!
Dead | 42879.37 | 41739.29 | 2.73% | OK!

## Slide 75
Structural aspects
Axial force | Hand calculation | ETABS | %Difference | < 10%
Slab | 558 | - | - | -
Beams | 412.36 | - | - | -
Column | 108 | - | - | -
Total | 1078.456 | 1029.1384 | 4.81% | OK!
1-stress strain check for column

## Slide 76
Hand calculation | ETABS | %Difference | < 10%
228.10 | 216.8 | 5.21% | OK!
2-stress strain check for beam
Structural aspects

## Slide 77
Hand calculation | ETABS | %Difference | < 10%
76.3154 | 72 | 5.99% | OK!
3-stress strain check for slab
Structural aspects

## Slide 78
Deflection check
From ETABS = 18.75 mm
Max. allowable Deflection =34.16 mm
Structural aspects

## Slide 79
Period check
period time = 0.373second ---- it’s OK!
T manual =Ct *(Hn) ^3/4.
Ct=0.0488.
Hn : Building height = 20.5m.
T manual =0.47 sec.
T manual = 1.4 * .47= 0.658sec.
T from ETABS shall be <= 1.4 * T hand calculation.
Structural aspects

## Slide 80
Drift Check
The design story drift (Δ) shall not exceed the allowable story drift ( Δa) as obtained from Table 12.12-1 in ASCE 7-10 for any story which is ≤ 0.015hx.
Structural aspects

## Slide 81
The displacement of each floor in both direction X and Y has to be less than delta limit. The delta limit
from the table below is less than Standard
Drift Check
Story | Height | Dis-x | Dis-Y | Drift-X | Drift- Y | Delta-X | Delta-Y | Delta Limit | Comment
0 | - | - | - | - | - | - | - | - | -
1 | 4400 | 1.479 | 0.241 | 1.479 | 0.241 | 5.69415 | 0.92785 | 66 | OK!
2 | 4400 | 0.353 | 0.632 | 1.832 | 0.391 | 7.0532 | 1.50535 | 66 | OK!
3 | 3650 | 0.419 | 0.827 | 0.066 | 0.195 | 0.2541 | 0.75075 | 73 | OK!
4 | 3650 | 0.788 | 1.473 | 0.369 | 0.646 | 1.42065 | 2.4871 | 73 | OK!
5 | 3000 | 0.769 | 1.592 | 1.557 | 0.119 | 5.99445 | 0.45815 | 60 | OK!
Structural aspects

## Slide 82
Base shear check
Direction | period | V manual | Vetabs | error
X | 0.373 | 4356.35 | 4248.56 | 2.54%
Y | 0.268 | 4356.35 | 4248.56 | 2.54%
Error is less than 5% so its OK!
Structural aspects

## Slide 83
Structural elements Design
Structural aspects

## Slide 84
Checking design members:
Basement 2
Basement 1
Structural aspects

## Slide 85
Ground floor
First Floor
Checking design members:
Structural aspects

## Slide 86
1. Slabs
Structural elements Design
Structural aspects

## Slide 87
1. Slabs
Structural elements Design
Structural aspects

## Slide 88
2. Beams
B2 Beams
B1 Beams
Structural elements Design
Structural aspects

## Slide 89
2. Beams
GF Beams
F1 Beams
Structural elements Design
Structural aspects

## Slide 90
2. Beams
Structural elements Design
Structural aspects

## Slide 91
2. Beams
Structural elements Design
Structural aspects

## Slide 92
3. Columns
Structural elements Design
Structural aspects

## Slide 93
3. Columns
Structural elements Design
Structural aspects

## Slide 94
4. Shear walls
Structural elements Design
Structural aspects

## Slide 95
5.Footings
Structural elements Design
Structural aspects

## Slide 96
6. Stairs
Structural elements Design
Structural aspects

## Slide 97
Electro-Mechanical Aspects

## Slide 98
Electro-Mechanical Aspects
Artificial Lighting Design:
Meeting Room:
Ambient Light Catalogue
Task Light Catalogue
Accent Light Catalogue

## Slide 99
Electro-Mechanical Aspects
Artificial Lighting Design:
Meeting Room:
Accent Light Catalogue
Meeting Table Result
General meeting room result

## Slide 100
Electro-Mechanical Aspects
Artificial Lighting Design:
Meeting Room:
UGR Calculation objects plan
UGR Results

## Slide 101
Electro-Mechanical Aspects
Artificial Lighting Design:
Meeting Room:

## Slide 102
Electro-Mechanical Aspects
Artificial Lighting Design:
Classroom:
Luminaire used in Classroom Catalogue
Classroom Results

## Slide 103
Electro-Mechanical Aspects
Artificial Lighting Design:
Classroom:
UGR Calculation objects plan
UGR Result

## Slide 104
Electro-Mechanical Aspects
Artificial Lighting Design:
Classroom:

## Slide 105
Electro-Mechanical Aspects
Artificial Lighting Design:
Computer Lab:
Computer Lab Results
UGR Calculation objects plan

## Slide 106
Electro-Mechanical Aspects
Artificial Lighting Design:
Computer Lab:
UGR Result

## Slide 107
Electro-Mechanical Aspects
Artificial Lighting Design:
Luminaires Distribution:
Luminaires Distribution in B2
Luminaires Distribution in B1

## Slide 108
Electro-Mechanical Aspects
Artificial Lighting Design:
Luminaires Distribution:
Luminaires Distribution in GF
Luminaires Distribution in FF

## Slide 109
Electro-Mechanical Aspects
HVAC System Design:
According to the simulation results on Design builder software the total heating load is equal 74.8 kW and the total cooling load is equal 105.11 kW. The system was designed on cooling load because it’s the higher value.
Outdoor and indoor units Catalogue

## Slide 110
Electro-Mechanical Aspects
HVAC System Design:
Slot Diffuser Catalogue
600x600 Diffuser Catalogue
Ventilation Fan catalogue
300x300 Exhaust catalogue

## Slide 111
Electro-Mechanical Aspects
HVAC System Design:
HVAC Distribution in B2
HVAC Distribution in B1

## Slide 112
Electro-Mechanical Aspects
HVAC System Design:
HVAC Distribution in GF
HVAC Distribution in FF

## Slide 113
Electro-Mechanical Aspects
HVAC System Design:

## Slide 114
Electro-Mechanical Aspects
Electrical Power Design:
Sockets Distribution:
Socket Distribution in B2
Socket Distribution in B1

## Slide 115
Electro-Mechanical Aspects
Electrical Power Design:
Sockets Distribution:
Socket Distribution in GF
Socket Distribution in FF

## Slide 116
Electro-Mechanical Aspects
Electrical Power Design:
Drop Voltage:
Resistance for Normal Load |  |  | 
Resistance wire (r) | maximum length (m) | wire area (m^2) | R ()
1.68E-08 | 30 | 0.0000025 | 0.2016
Current for Normal Load |  |  | 
Power (watt) | Volt (v) | Factor | I load (Amp)
1000 | 220 | 0.9 | 5.1
Drop Voltage for Normal Load |  |  |  | 
I load (Amp) | R (W) | Drop Voltage | Drop Voltage % | Check
5.1 | 0.2016 | 1.0 | 0. 46 | ok
Resistance for Special Load |  |  | 
Resistance wire (r) | maximum length (m) | wire area (m^2) | R ()
1.68E-08 | 30 | 0.0000025 | 0.2016
Current for Special Load |  |  | 
Power (watt) | Volt (v) | Factor | I load (Amp)
1500 | 220 | 0.9 | 7.6
Drop Voltage for Special Load |  |  |  | 
I load (Amp) | R (W) | Drop Voltage | Drop Voltage % | Check
7.6 | 0.2016 | 1.5 | 0.70 | ok
Voltage Drop for normal power socket
Voltage Drop for special power socket
<5% so its ok

## Slide 117
Electro-Mechanical Aspects
Electrical Power Design:
Distribution Boards Design:
DB | No. of sockets | Normal load |  | Special load | Lighting Load | Total power | I load | I C.B | I Cable | C.B | Cable IEC | Cable size | No. of power branches | No. of lighting branches
- | - | Watt | Watt | Watt | Watt | Watt | Amp | Amp | Amp | Amp | Amp | mm^2 | - | -
DBGa | 26 | 250 | 6500 | 1500 | 1414 | 4581.2 | 23.14 | 26.61 | 30.60 | 36 | 36 | 6 | 10 | 6
DBGb | 19 | 250 | 4750 | 1500 | 1239 | 3916.2 | 19.78 | 22.75 | 26.16 | 30 | 36 | 6 | 8 | 5
DBGa-UPS | 0 | 250 | 0 | 0 | 1188 | 950.4 | 4.80 | 5.52 | 6.35 | 10 | 16 | 2.5 | 0 | 8
DBGb-UPS | 0 | 250 | 0 | 0 | 1041 | 832.8 | 4.21 | 4.84 | 5.56 | 10 | 16 | 2.5 | 0 | 7
Distribution Boards Load Calculation for Ground Floor

## Slide 118
Electro-Mechanical Aspects
Electrical Power Design:
Distribution Boards Design:
DB | No. of sockets | Normal load |  | Special load | Lighting Load | Total power | I load | I C.B | I Cable | C.B | Cable IEC | Cable size | No. of power branches | No. of lighting branches
- | - | Watt | Watt | Watt | Watt | Watt | Amp | Amp | Amp | Amp | Amp | mm^2 | - | -
DBB2a | 34 | 250 | 8500 | 1500 | 328 | 4312.4 | 21.78 | 25.05 | 28.80 | 30 | 36 | 6 | 12 | 6
DBB2b (3 phase) | 39 | 250 | 9750 | 3000 | 961 | 6693.8 | 33.81 | 38.88 | 44.71 | 50 | 50 | 10 | 14 | 6
DBLAB1 (3 phase) | 57 | 250 | 14250 | 1500 | 228 | 5957.4 | 30.09 | 34.60 | 39.79 | 40 | 50 | 10 | 19 | 6
DBB2a-UPS | 4 | 250 | 1000 | 4500 | 720 | 5376 | 27.15 | 31.22 | 35.91 | 36 | 44 | 10 | 2 | 7
DBB2a-UPS (Elevator C.B) | - | - | - | - | - | 4500 | 20.45 | 23.52 | 27.05 | 32 |  |  | - | -
DBB2b-UPS | 0 | 250 | 0 | 0 | 1070 | 856 | 4.32 | 4.97 | 5.72 | 10 | 16 | 2.5 | 2 | 7
Main Distribution Board |  |  |  |  |  | 
DB | Total power | I load | I C.B | I Cable | C.B | Cable size
- | Watt | Amp | Amp | Amp | Amp | mm^2
MDB ( 3 phase ) | 27695.6 | 76.93 | 88.47 | 101.74 | - | -
each phase | 9231.87 | 46.63 | 53.6194 | 61.662 | 66 | 16
Main distribution and first floor load calculation

## Slide 119
Electro-Mechanical Aspects
Electrical Power Design:
Generator selection:
Backup system should work automatically when an electrical cut occurs, so a UPS system installed to feed selected luminaires, sockets and the elevator with enough power to work normally.
The total power that UPS must feed is 14125 watt
Reserve capacity = Total power * 0.25 = 14125 * 0.25 = 3531.25 watt
Generator size = Total power + Reserve capacity = 14125 + 3531.24 = 17656.25 watt
So the selected capacity for the generator is 20 kW 3 Phase

## Slide 120
Electro-Mechanical Aspects
Fire alarm and Firefighting system:
Sample for detectors location
Sample for fire hose location

## Slide 121
Electro-Mechanical Aspects
Fire alarm and Firefighting system:
Sample for extinguisher location
FM200 Suppression System

## Slide 122
Electro-Mechanical Aspects
Fire alarm and Firefighting system:
Evacuation Plans:
Evacuation routes in B2
Evacuation routes in B1

## Slide 123
Electro-Mechanical Aspects
Fire alarm and Firefighting system:
Evacuation Plans:
Evacuation routes in GF
Evacuation routes in FF

## Slide 124
Electro-Mechanical Aspects
Water Supply System:
Tanks Capacity and Distribution:
Required water per day = 600 student * 18 L/day*student = 10800 L/Day
In Nablus city water pumped by municipality every 3 days, so enough water should save in tanks to serve for 3 days.
The total amount of water for each cycle = required water per day * 3 days = 10800 L/Day * 3 Days = 32400 L
Tanks with 2000 Liter capacity were used.
Total number of tanks needed in the school = 32400 L / 2000 L = 16.2 Tank
So 17 Royal tanks with 2000 L capacity were used

## Slide 125
Electro-Mechanical Aspects
Water Supply System:
Tanks Capacity and Distribution:
Tanks Distribution on the Roof

## Slide 126
Electro-Mechanical Aspects
Water Supply System:
Water Supply Pipes Sizing:
Branch | Fixture type | No. of fixture | Load value | WSFU | Total WSFU | Demand gpm | PVC Horizontal Ꝋ | Horizontal Ꝋ | Vertical Ꝋ
T1-FF | Water closet | 7 | 5 | 35 | 55 | 30 | 3/4" | 1.5" | 2"
 | Lavatory | 8 | 2 | 16 |  |  |  |  | 
 | Sink | 1 | 4 | 4 |  |  |  |  | 
T1-GF | Water closet | 8 | 5 | 40 | 54 | 29 |  | 1.5" | 
 | Lavatory | 7 | 2 | 14 |  |  |  |  | 
T1-B2 | Sink | 10 | 4 | 40 | 40 | 25 | 3/4" | 1.5" | 
T2-B1 | Water closet | 8 | 5 | 40 | 48 | 28 |  | 1.5" | 2"
 | Lavatory | 4 | 2 | 8 |  |  |  |  | 
T2-B2 | Water closet | 9 | 5 | 45 | 61 | 33 |  | 1.5" | 
 | Lavatory | 6 | 2 | 12 |  |  |  |  | 
 | Sink | 1 | 4 | 4 |  |  |  |  | 
T3-GF | Water closet | 2 | 5 | 10 | 14 | 10 | 3/4" | 1" | 2"
 | Lavatory | 2 | 2 | 4 |  |  |  |  | 
T3-B1 | Water closet | 10 | 5 | 50 | 64 | 35 |  | 1.5" | 
 | Lavatory | 7 | 2 | 14 |  |  |  |  | 
T3-B2 | Water closet | 2 | 5 | 10 | 18 | 14 |  | 1.25" | 
 | Lavatory | 2 | 2 | 4 |  |  |  |  | 
 | Sink | 1 | 4 | 4 |  |  |  |  | 
Pipe Sizing for the whole group branches
Sample for PVC horizontal branches distribution

## Slide 127
Electro-Mechanical Aspects
Water Supply System:
Pump Selection:
Branch |  | Pressure without losses (psi) | Losses (psi) | Pressure with Losses (psi) | Check
T1 | B2 | 25.73 | 10.34 | 15.39 | ok
 | GF | 13.23 | 9.22 | 4.01 | not ok
 | FF | 8.05 | 9.36 | -1.31 | not ok
T2 | B2 | 25.73 | 5.06 | 20.67 | ok
 | B1 | 19.485 | 4.61 | 14.875 | ok
T3 | B2 | 20.55 | 2.48 | 18.07 | ok
 | B1 | 15.36 | 2.63 | 12.73 | ok
 | GF | 8.05 | 1.25 | 6.8 | not ok
water pump catalogue for T1 branch

## Slide 128
Electro-Mechanical Aspects
Water Supply System:
Pump Selection:
water pump catalogue for T3 branch
water pump catalogue for firefighting system

## Slide 129
Electro-Mechanical Aspects
Water Supply System:
Hot Water Design:
The total amount of required hot water = No. of students * Required hot water per day
= 570 Student * 2.3 L/Day*Student = 1311 L / Day.
So use 5 electric boilers with 125 L capacity for students W.C and 6 electric boilers of 50 L capacity for teachers’ rooms
125 L Electric Boiler catalogue
50 L Electric Boiler catalogue

## Slide 130
Electro-Mechanical Aspects
Drainage and Rain Water System:
Drainage Pipes Design:
Stack No. | Floor | Type of unit | No pf units | DFU | Total DFU | Horizontal Drains Ꝋ | Stack Ꝋ
Stack 1 | B1 | W.C | 8 | 4 | 32 | 4" 1% | 4"
 |  | Lavatory | 4 | 1 | 4 | 2" 2% | 
 | B2 | W.C | 9 | 4 | 36 | 4" 1% | 
 |  | Lavatory | 7 | 1 | 7 | 2" 2% | 
Sum |  |  |  |  | 79 |  | 
Stack 2 | GF | W.C | 8 | 4 | 32 | 4" 1% | 4"
 |  | Lavatory | 7 | 1 | 7 | 2" 2% | 
 |  | Floor trap | 1 | 3 | 3 | 2" 2% | 
 | B2 | Sink | 10 | 2 | 20 | 2" 2% | 
Sum |  |  |  |  | 62 |  | 
Stack 3 | FF | W.C | 5 | 4 | 20 | 4" 1% | 4"
 |  | Lavatory | 6 | 1 | 6 | 2" 2% | 
 |  | Floor trap | 1 | 3 | 3 | 2" 2% | 
 | GF | Floor trap | 2 | 3 | 6 | 2" 2% | 
 | B1 | Floor trap | 2 | 3 | 6 | 2" 2% | 
Sum |  |  |  |  | 41 |  | 
Stack 4 | FF | W.C | 2 | 4 | 8 | 4" 1% | 4"
 |  | Lavatory | 2 | 1 | 2 | 2" 2% | 
 |  | Sink | 1 | 2 | 2 | 2" 2% | 
Sum |  |  |  |  | 12 |  | 
Stack 5 | GF | W.C | 2 | 4 | 8 | 4" 1% | 4"
 |  | Lavatory | 2 | 1 | 2 | 2" 2% | 
Sum |  |  |  |  | 10 |  | 
Stack 6 | FF | Floor trap | 1 | 3 | 3 | 2" 2% | 4"
 | GF | Floor trap | 1 | 3 | 3 | 2" 2% | 
 | B1 | W.C | 5 | 4 | 20 | 4" 1% | 
 |  | Lavatory | 5 | 1 | 5 | 2" 2% | 
 |  | Floor trap | 1 | 3 | 3 | 2" 2% | 
 | B2 | Floor trap | 1 | 3 | 3 | 2" 2% | 
Sum |  |  |  |  | 37 |  | 
Stack 7 | B1 | W.C | 5 | 4 | 20 | 4" 1% | 4"
 |  | Lavatory | 2 | 1 | 2 | 2" 2% | 
 | B2 | W.C | 2 | 4 | 8 | 4" 1% | 
 |  | Lavatory | 2 | 1 | 2 | 2" 2% | 
Sum |  |  |  |  | 32 |  | 
Sample for drainage system design

## Slide 131
Electro-Mechanical Aspects
Drainage and Rain Water System:

## Slide 132
Electro-Mechanical Aspects
Drainage and Rain Water System:
Rain Water System Design:
This system aims to design correct drainage of rain water to avoid problems due to accumulation of the rainwater on roof, water seepage, stains and structural side effects

## Slide 133
Electro-Mechanical Aspects
Vertical Transportation:
Elevator Selection:
Standard for Handicapped Elevator
Selected Elevator Catalogue

## Slide 134
Electro-Mechanical Aspects
Acoustical Design:
STC for Internal Partition

## Slide 135
Electro-Mechanical Aspects
Acoustical Design:
STC for External Walls
Where the outdoor background noise level is between 76 dBA and 80 dBA, then the OITC should be not less than 50

## Slide 136
Electro-Mechanical Aspects
Acoustical Design:
IIC for Floor
IIC ratings for floor-ceiling assemblies above core learning spaces should be at least IIC-45 and preferably IIC-50 (measured without carpeting on the floor).

## Slide 137
FREQ. | TOTAL | SABINE | NOR-ER | MIL-SE
 | ABSPT. | RT(60) | RT(60) | RT(60)
63Hz | 12.602 | 1.25 | 0.78 | 1.19
125Hz | 10.428 | 1.39 | 0.96 | 1.35
250Hz | 12.673 | 0.93 | 0.88 | 0.90
500Hz | 26.449 | 0.62 | 1.01 | 0.46
1kHz | 49.201 | 0.35 | 0.74 | 0.15
2kHz | 50.698 | 0.32 | 0.67 | 0.13
4kHz | 42.957 | 0.36 | 0.67 | 0.21
8kHz | 40.382 | 0.31 | 0.52 | 0.21
16kHz | 38.879 | 0.31 | 0.50 | 0.22
Classroom | 0.6-0.8
Electro-Mechanical Aspects
Acoustical Design:
RT60 for Classroom

## Slide 138
FREQ. | TOTAL | SABINE | NOR-ER | MIL-SE
 | ABSPT. | RT(60) | RT(60) | RT(60)
63Hz | 16.653 | 1.43 | 0.99 | 1.36
125Hz | 13.683 | 1.59 | 1.18 | 1.54
250Hz | 15.491 | 1.18 | 1.12 | 1.15
500Hz | 28.776 | 0.76 | 1.26 | 0.61
1kHz | 53.192 | 0.46 | 0.88 | 0.20
2kHz | 54.876 | 0.43 | 0.79 | 0.17
4kHz | 46.744 | 0.45 | 0.75 | 0.28
8kHz | 43.790 | 0.39 | 0.58 | 0.27
16kHz | 42.394 | 0.39 | 0.55 | 0.28
Recommended RT60 for library = 0.6 to 0.8
Electro-Mechanical Aspects
Acoustical Design:
RT60 for Library

## Slide 139
SPL
Electro-Mechanical Aspects
Acoustical Design:
Ease Modeling for Cafeteria

## Slide 140
Total Sound pressure level Values on areas
Articulation Values on areas
Electro-Mechanical Aspects
Acoustical Design:
Ease Results for Cafeteria

## Slide 141
Direct Sound pressure level Values on areas
Articulation index Values on areas
Electro-Mechanical Aspects
Acoustical Design:
Ease Results for Cafeteria

## Slide 142
Integrated System:
B2 Integrated Plan :

## Slide 143
Integrated System:
B1 Integrated Plan :

## Slide 144
Integrated System:
GF Integrated Plan :

## Slide 145
Integrated System:
FF Integrated Plan :

## Slide 146
Quantity Surveying and Cost Estimation
The total cost for the school = 4,295,858 Nis, including material, labor and equipment cost. The table below show a brief summary for the main components of the project cost.
Item | Total Cost (NIS)
Earth Work | 114,900
Construction Work | 1,352,904
Finishes Work | 1,649,476
Electrical Work | 442,680
Mechanical Work | 735,898
Total Project Cost | 4,295,858

## Slide 147
Thank you