## Slide 1
Studying Geothermal Heat Pump in Palestine

## Slide 2: Prepared By : Ahmad Khaled- Mohanad Khalelia- Nedal Saleh
Graduation Project
Supervised By :
Miss. Hala Hadad

## Slide 3
Site Analysis.
Architectural Design..
Structural Design.
Geothermal system design.
Cost Estimation
Presentation Outline

## Slide 4
Project Information
This Graduation Project Interested in designing Geothermal heating and cooling system for residential building, and compare with traditional HVAC system.
General Overview

## Slide 5
Site Location.
Soil Analysis and topography.
Climate.
Temperature.
Wind.
Shadows.
Site Analysis

## Slide 6
Site Location

## Slide 7
Soil Analysis and topography.

## Slide 8
Temperature

## Slide 9
Wind

## Slide 10
Shadows

## Slide 11
Site plan.
Ground floor.
Elevations.
Sections.
Environmental analysis.
Sun path and shadows.
Natural lighting.
Insolation analysis.
Architectural Design

## Slide 12
Site Plan

## Slide 13
Ground floor

## Slide 14
South elevation

## Slide 15
North elevation

## Slide 16
East elevation

## Slide 17
West elevation

## Slide 18
Section A-A

## Slide 19
Section B-B

## Slide 20
Sun path and shadows
Summer

## Slide 21
Sun path and shadows
Winter

## Slide 22
Daylight level

## Slide 23
Daylight factor

## Slide 24
Insolation Analysis

## Slide 25
Structural Design
Design data .
Slab design.
Beam design.
Column design.
Footing design.

## Slide 26
Design data
Compressive strength of concrete (f'c): The compressive strength of concrete for beams, columns, slabs and footing was chosen as =280 Kg/cm2.
Yielding strength of steel (Fy ): The yield strength of steel for flexure equal = 4200 Kg/ cm2 and for shear reinforcement equal = 4200 Kg/ cm2 .
Unit weights of materials: Concrete = 2500 Kg/ m3, Block=1000 Kg/ m3.
Superimposed dead load=300Kg/ m2 , Live load=250Kg/ m2

## Slide 27
Slab design
Compatibility check

## Slide 28
Reinforcement Details
Slabs are designed as one way ribbed slab with thickness =25cm

## Slide 29
Beam Design
حديد مكسوح | Bottom reinforcement | Upper reinforcement | Beam#
3 ɸ16 | 7 ɸ14 | 4 ɸ12 | 4
حديد مكسوح | Bottom Steal | Upper Steel | Beam#
3 ɸ14 | 6 ɸ14 | 4 ɸ12 | 1,5
3 ɸ16 | 7 ɸ16 | 4 ɸ12 | 2,3
3 ɸ12 | 3 ɸ12 | 3 ɸ12 | 6,8,9(secondary beams)
3 ɸ16 | 3 ɸ14 | 3 ɸ12 | 7

## Slide 30
Beam Design

## Slide 31
Column design

## Slide 32
Footing design

## Slide 33
Geothermal system design.
Introduction.
Design step.
Choose geothermal system type.
Building load.
Heat pump selection.
Pipe size and length.
Properties of trenches.
Land required.

## Slide 34
Introduction

## Slide 35
Design step

## Slide 36
Choose geothermal system type
The determination of geothermal heat pump system for heating and cooling type depend on many factor:
Site properties
Geology
Hydrology
Land Availability
Topography
Building type
Natural resource
So we choose the horizontal close loop system

## Slide 37
Building load
Building properties
External wall Internal wall
Layer name | Width | Density
Stone | 0.07 | 2300
Concrete | 0.1 | 2300
Polystyrene | 0.02 | 46
Block | 0.1 | 1040
Plaster | 0.007 | 1250
Layer name | Width | Density
Plaster | 0.007 | 1250
Block | 0.1 | 1040
Plaster | 0.007 | 1250

## Slide 38
Celling Floor
Layer name | Width | Density
Concrete | 0.25 | 2300
Polystyrene | 0.02 | 46
Air gap | 0.05 | 1.3
Gipson board | 0.007 | 1250
Layer name | Width | Density
Soil | 1.5 | 1300
Concrete | 0.15 | 2800
Concrete screed | 0.005 | 2000
Ceramic tiles | 0.01 | 1900

## Slide 39
Window Door
Layer name | Width | Density
Glass standard | 0.006 | 2300
Air gap | 0.03 | 1.3
Glass standard | 0.006 | 2300
Layer name | Width | Density
Wood pine | 0.04 | 550

## Slide 40
Weather data
Weather data as we describe before.

## Slide 41
Heating & Cooling Load
Max Cooling: 15518 W Max Heating: 23576 W

## Slide 42
Heat pump selection
The selection of heat pump depend on:
Geothermal system type
Project system is used a closed horizontal system.

## Slide 43
Assistant HVAC system
Assistant HVAC system used is Fan coil with two pipe heating/cooling, single coil system.

## Slide 44
Assistant HVAC system
Assistant HVAC system used is Fan coil with two pipe heating/cooling, single coil system.

## Slide 45
Building load
Heating load is 23.576 KW, and the cooling load is 15.518 KW
Pump properties
The Assistant HVAC system used is Fan coil, so we choose water to water ground heat pump.

## Slide 46
From this data the selected type of heat pump is
RW Series: Commercial Reversible Chiller - 60 Hz (8-50 Tons).
AHRI/ASHRAE/ISO 13256-2 Water-to-Water Ratings
Model | Capacity Modulation | Flow rate |  |  | Ground Loop Heat Pump |  |  |  | 
 |  |  |  |  | Cooling Full EST 25°C Part EST 20°C ELT 12°C |  | Heating Full EST 0°C Part ELT 5°C ELT 40°C |  | 
 |  | Source L/S |  | Load L/S | Capacity Watts | EER | Capacity Watts |  | COP
096 | Full | 1.5 | 1.5 |  | 29,894 | 5.0 | 24,619 | 3.1 | 
 | Part | 1.5 | 1.5 |  | 16,706 | 6.6 | 14,361 | 3,5 | 

## Slide 47
Pipe length and size
Pipe size
The table below shown the pipe size and the maximum and minimum flow rate in Schedule 40 pipe for water
Pipe size (in) | Min Flow rate (gpm) | Max Flow rate (gpm)
3/4 | 1 | 20
1 | 2 | 30
1 1/4 | 2 | 50
From heat pump the flow rate is 1.5 L/S which is equal 23.77 gpm, then the pipe size is 1 in.

## Slide 48
Pipe length
The not enough date about soil thermal resistance and ground temperature in Nablus city, we used method two to determine the pipe length.
For horizontal (Two pipes per trench): L=44m/KW (155.5m/ton).
Lc = 683m Lh = 1038m
Because we used the same pipe for both heating and cooling we take the max. length that is 1038m.

## Slide 49
Properties of trenches
Number | depth | length | width | Area
17 | 2 | 31 | 0.7 | 21.7
Total |  | 527 |  | 368.9

## Slide 50
Land required

## Slide 51
Cost estimation
Traditional HVAC System Cost
Geothermal System Cost

## Slide 52
Traditional HVAC System Cost
Initial Cost
The max. building load is 23.576 KW (7 ton), and the building has the 6 zones to heat and cool, So split unit used is:
Room | Number | Capacity of split unit ( ton) | Price ( $)
Bedroom | 3 | 1 | 1500
Office room | 1 | 1 | 500
Living room | 1 | 1.5 | 700
Guest room | 1 | 1.5 | 700
Total | 6 | 7 | 3400

## Slide 53
Running Cost
The table below show the average properties of deferent type of split unit
Capacity ( ton) | Capacity (KW) |  | Power (KWh)
 | Heating | Cooling | 
1 | 3.81 | 3.51 | 1.3
1.5 | 5.87 | 5.27 | 2
2 | 7.92 | 7.02 | 3.74

## Slide 54
Geothermal System Cost
Initial cost
The initial cost depend on
Drilling Machine cost
Labor installation cost
Assistants fan coil unit
Maintenance cost
Running Cost
The running cost depend on the performance and the capacity of heat pump

## Slide 55
Summery
System | Initial cost ($) | Running cost ($) | Maintenance cost ($) | Total cost ($)
HVAC | 3400 | 3709.5 | 285 | 7394.5
Geothermal | 12354 | 2459.5 | 145 | 14958.5

## Slide 56
From this figure we can see that after 7 year, geothermal system cost is equal to HVAC system cost.
So is considered as a good system in Palestine.
because
High initial cost of the geothermal system and low initial cost of the traditional system.
low running cost of the geothermal system and high running cost of the traditional system.
The running cost of the geothermal system is almost 20% less than the HVAC system
The main disadvantage of this geothermal system is the high initial cost, on the other hand it consider as environmentally friendly.
High maintenance cost of traditional system, and low maintenance cost of geothermal system.