## Slide 1: Integrated Design of a Secondary School
Graduation Project 2
Prepared by:-
Qamar Nouri
Khawla Zaben
Ranen Hamdan
Supervisor:-
Eng. Nirmeen Al-Barq

## Slide 2: Outline
Site analysis
Architectural
Structural
Electrical
Mechanical
Quantity surviving
Environmental

## Slide 3: Site Analysis
Located in Al-Maajen, 5.3 km away from Nablus.
Surroundings.
Land Area = 4949 m2
Land slope of around 11%.
Building Area = 4500m2
Parking.

## Slide 4: Architectural Design
Building Area = 5421 m2
Four Floors

## Slide 5: Basement Floor Plan
Floor Area= 831m 2
Spaces: Mechanical and Electrical Rooms, Stores, Music Room
Architectural Design

## Slide 6: Ground Floor Plan
Floor Area= 1530 m2
Two Blocks
Spaces: Multipurpose, Meeting Room, Administration Area
Architectural Design

## Slide 7: First Floor Plan
Architectural Design

## Slide 8: Second Floor Plan
Architectural Design

## Slide 9: Elevations
Southern Elevation
Architectural Design

## Slide 10: Northern Elevation
Architectural Design
Elevations

## Slide 11: Western Elevation
Architectural Design
Elevations

## Slide 12: Eastern Elevation
Architectural Design
Elevations

## Slide 13: Sections
Architectural Design

## Slide 14
Structural and Seismic Design
Structural Design

## Slide 15: Structural Design
Codes of Design:
The American Concrete Institute code ACI 318-08.
The seismic design according to UBC-97.
The analysis and design were conducted using ETABS, SAP, and SAFE programs.

## Slide 16: Structural Design
Design Criteria:
Concrete Compressive Strength :
f’c = 28 Mpa For Columns, Shear walls and Footings.
f’c = 24 Mpa For Slabs and Beams.
Yielding Strength of Steel:
The Yield Strength of Steel Fy = 420 Mpa.

## Slide 17: Structural Design
Loads:
Live Load = 5 kN/m2.
Super Imposed Dead Load for One Way Ribbed Slab = 6.8 kN/m2.
Super Imposed Dead Load for Two Way Ribbed Slab = 6 kN/m2.
Dead load

## Slide 18: Structural Design
Depth (cm) | System of Slab
40 | One way Ribbed Slab
40 | Two Way Ribbed Slab
Thickness of Slabs:

## Slide 19: Structural Design
Sections of Beams used in Design:
Width (cm) | Depth (cm) | Section Name
50 | 75 | Main Beam
35 | 40 | Secondary Beam
Dimensions (cm) | Column Name
60x35 | C60x35
80x60 | C80x60
80x30 | C80x35
80x40 | C80x40
Sections of Columns used in Design:

## Slide 20: Structural Design
The Distribution of Columns and Shear Walls:

## Slide 21: Structural Design
Expansion Joint at 35m.

## Slide 22: Structural Design
3D Modeling From ETABS Program:
First Block
Second Block

## Slide 23: Structural Design
Compatibility Check:
First Block
Second Block

## Slide 24: Structural Design
Equilibrium Check:
Difference (%) | Calculations from ETABS (kN) | Manual Calculation (kN) | Load
0.2 | 27178 | 27123 | Dead Load
0.07 | 15775 | 15787 | Live Load
0.7 | 34833 | 34588 | Super Imposed Dead Load
Difference (%) | Calculations from ETABS (kN) | Manual Calculation (kN) | Load
3.6 | 19185 | 18514 | Dead Load
0.19 | 11324 | 11346 | Live Load
1.4 | 21689 | 22006 | Super Imposed Dead Load
For First Block
For Second Block

## Slide 25: Structural Design
Samples for Internal Forces Check for Beams:
For First Block
For Second Block

## Slide 26: Structural Design
Internal Forces Check for Beams:
Difference (%) | Calculations from ETABS (kN.m) | Manual Calculation (kN.m) | Column Type
1.95 | 1295.77 | 1321.27 | Edge
5.9 | 1836.50 | 1727.76 | Interior
9.25 | 1294.5 | 1174.5 | Another Interior
Difference (%) | Calculations from ETABS (kN.m) | Manual Calculation (kN.m) | Load
9.3 | 907.37 | 822.30 | Edge
2.5 | 1890.50 | 1937.80 | Interior
3.6 | 1474.15 | 1420.67 | Another Interior
For First Block
For Second Block

## Slide 27: Structural Design
Samples for Internal Forces Check for Slabs:
For First Block
For Second Block

## Slide 28: Structural Design
Difference (%) | Calculations from ETABS (kN.m) | Manual Calculation (kN.m) | Column Type
8.36 | 66 | 60.48 | S1
7.3 | 109 | 100.90 | S2
8.6 | 11.50 | 10.50 | S3
Difference (%) | Calculations from ETABS (kN.m) | Manual Calculation (kN.m) | Load
4.1 | 120 | 124.97 | S1
10 | 115 | 126.80 | S2
9 | 86.50 | 94.50 | S3
Internal Forces Check for Slabs:
For First Block
For Second Block

## Slide 29: Structural Design
For First Block
For Second Block
Samples for Internal Forces Check for Columns:

## Slide 30: Structural Design
Internal Force Check for Columns:
Difference (%) | Calculations from ETABS (kN) | Manual Calculation (kN) | Load
2.3 | 675.42 | 659.58 | Corner
8.4 | 3054.25 | 2796.35 | Edge
7.25 | 3180.42 | 2949.72 | Middle
Difference (%) | Calculations from ETABS (kN) | Manual Calculation (kN) | Load
7.6 | 930.75 | 1002.3 | Corner
1.9 | 2154.35 | 2195.86 | Edge
3.1 | 5827.96 | 5645.77 | Middle
For First Block
For Second Block

## Slide 31: Structural Design
Seismic Design Using Response Spectrum - UBC 97:
Mass of Building Defined as mass source including 100% of dead and super imposed dead load and 25% of live load.
Nablus City with a Zone Factor (Z) equals 0.2
The soil type is SC which are clay and silt soil. (250 kN/m2 soil bearing capacity).
Overstrength Factor (R) equals 5.5 for Sway Intermediate Concrete Frame Structure.
Importance Factor (I) equals 1.25
Acceleration Seismic Coefficient (Ca) equals 0.24
Velocity Seismic Coefficient (Cv) = 0.32

## Slide 32: Structural Design
Period Check:
Ty (Sec) | Tx (Sec) | 
0.55 | 0.55 | Manual Value
0.46 | 0.66 | ETABS Value
Ty (Sec) | Tx (Sec) | 
0.44 | 0.44 | Manual Value
0.35 | 0.40 | ETABS Value
For First Block
For Second Block

## Slide 33: Structural Design
Modal Participating Mass Ratios Check (Second Block):
Modal Participating Mass Ratios |  |  |  |  |  |  |  | 
Case | Mode | Period sec | UX | UY | UZ | Sum UX | Sum UY | Sum UZ
Modal | 1 | 0.57 | 0.0156 | 0.2188 | 0 | 0.0156 | 0.2188 | 0
Modal | 2 | 0.42 | 0.6253 | 0.1442 | 0 | 0.6409 | 0.363 | 0
Modal | 3 | 0.347 | 0.1014 | 0.4392 | 0 | 0.7423 | 0.8022 | 0
Modal | 4 | 0.25 | 0.0006 | 0.0206 | 0 | 0.7428 | 0.8228 | 0
Modal | 5 | 0.194 | 0.0114 | 0.0392 | 0 | 0.7542 | 0.862 | 0
Modal | 6 | 0.168 | 0.0028 | 0.0098 | 0 | 0.757 | 0.8718 | 0
Modal | 7 | 0.131 | 0.0043 | 0.0273 | 0 | 0.7613 | 0.8992 | 0
Modal | 8 | 0.125 | 0.0577 | 0.0653 | 0 | 0.8189 | 0.9644 | 0
Modal | 9 | 0.108 | 0.0064 | 0.0001 | 0 | 0.8253 | 0.9645 | 0
Modal | 10 | 0.1 | 5.55E-06 | 0.0141 | 0 | 0.8253 | 0.9787 | 0
Modal | 11 | 0.093 | 0.0848 | 0.0011 | 0 | 0.9101 | 0.9798 | 0
Modal | 12 | 0.078 | 0.0103 | 0.0015 | 0 | 0.9204 | 0.9813 | 0
12 Modes satisfy percentage higher than 90%

## Slide 34: Structural Design
Base Shear Check:
V ETABS (kN) | V manual (kN) | T (Sec) | Load Case
8816.19 | 8816.19 | 0.55 | EQx
10541.09 | 10541.09 | 0.46 | EQy
V ETABS (kN) | V manual (kN) | T (Sec) | Load Case
6653.87 | 6653.87 | 0.40 | EQx
6653.87 | 6653.87 | 0.35 | EQy
For First Block
For Second Block

## Slide 35: Structural Design
For First Block
For Second Block
Drift Check:
Delta Limit (mm) | Delta y (mm) | Delta x (mm) | Story
100 | 4.04 | 0.85 | 1
100 | 12.94 | 33.92 | 2
100 | 16.98 | 32.96 | 3
100 | 15.05 | 24.45 | 4
Delta Limit (mm) | Delta y (mm) | Delta x (mm) | Story
100 | 6.93 | 10.78 | 1
100 | 10.78 | 14.63 | 2
100 | 11.17 | 15.79 | 3

## Slide 36: Structural Design
Slab Structural Systems for Design:
(one way ribbed slab and two way ribbed slab).

## Slide 37: Structural Design
Slab Structural Systems for Design:
(one way ribbed slab and two way ribbed slab).

## Slide 38: Structural Design
Typical Section in One Way Ribbed Slab:

## Slide 39: Structural Design
Typical Section in Two Way Ribbed Slab:

## Slide 40: Structural Design
Reinforcement for Beams:

## Slide 41: Structural Design
Beams Layout:

## Slide 42: Structural Design
Main Beam Detailing:

## Slide 43: Structural Design
Main Beam Sections:

## Slide 44: Structural Design
Secondary Beam Detailing:

## Slide 45: Structural Design
Secondary Beam Sections:

## Slide 46: Structural Design
Table of Reinforcement Columns:

## Slide 47: Structural Design
Column Design Detailing:

## Slide 48: Structural Design
Shear wall label | Pu (kN) | Mu (kN.m) | Vu (kN) | Longitudinal reinforcement | Transverse reinforcement
SW1 | 7242 | 30241 | 1643 | 1Ø14/200mm in each layer | 1Ø12/250mm in each layer
SW2 | 6485 | 17395 | 2694 | 1Ø14/150mm in each layer | 1Ø12/150mm in each layer
SW3 | 6899 | 25520 | 2492 | 1Ø14/250mm in each layer | 1Ø12/250mm in each layer
SW4 | 4873 | 19539 | 5218 | 1Ø16/200mm in each layer | 1Ø12/100mm in each layer
Reinforcement for Shear Walls:

## Slide 49: Structural Design
Shear Wall Detailing:

## Slide 50: Structural Design
Reinforcement for Footings:

## Slide 51: Structural Design
Footings Layout:

## Slide 52: Structural Design
Plan for F3
Section for F3
Detailing for Single Footing:

## Slide 53: Structural Design
Plan for F7
Section for F7
Detailing for Combined Footing:

## Slide 54: Structural Design
Staircase Design:

## Slide 55: Structural Design
Staircase Slab Design:

## Slide 56: Electrical Design
Sockets Distributions
Artificial Lighting Design
Sound Reinforcement System
Electrical Distribution Board

## Slide 57: Electrical Design
Sockets Distributions:

## Slide 58: Electrical Design
Space |  | Illuminance (Eavg) | Standard Illuminance (Eavg) | Uniformity | Glare
Classroom | Students Tables | 482 | 300 | 0.62 | 18.8
 | Green Board | 547 | 500 | 0.64 | 
Space |  | Illuminance (Eavg) | Standard Illuminance (Eavg) | Uniformity | Glare
Classroom | Students Tables | 482 | 300 |  | 
 | Green Board | 547 | 500 |  | 
Headmaster Office | On the desk | 581 | 500 | 0 | 18.6
 | Workplane | 582 | 500 |  | 
Headmaster Office | On the desk | 581 | 500 |  | 
 | Workplane | 582 | 500 |  | 
Artificial Lighting Design:
Teachers Room | 313 | 300 | 0.69 | All values
Teachers Room | 313 | 300 |  | 

## Slide 59: Electrical Design
Artificial Lighting Design:
Space |  | Illuminance (Eavg) | Standard Illuminance | Uniformity | Glare
Computers Laboratory |  | 343 | 300 | 0.6 | All values
Library | Reading area | 566 | 500 | 0.6 | All values
 | Book shelves | 200 | 200 | 0.6 | 
Cafeteria |  | 306 | 200 | 0.7 | 
Space |  | Illuminance (Eavg) | Standard Illuminance | Uniformity | Glare
Computers Laboratory |  | 343 | 300 | 0.6 | 
Library | Reading area | 566 | 500 | 0.6 | 
 | Book shelves | 200 | 200 | 0.6 | 
Cafeteria |  | 306 | 200 | 0.7 | 
Surface | Reflection Factor
Ceiling | 70 %
Walls | 50%
Floor | 20%

## Slide 60
Luminaire Type: Thorlux Lighting - KE18958 Kanby EVO - Low Glare – SMART.
Company name: thorlux.
Lamp luminous flux = 6510 lumen.
Power= 49 watt.
Luminous efficacy: 132.9 lm/w.
Colorimetric data: CCT 4000 K, CRI 80.
Used in Classrooms, Library and Headmaster Office.
Electrical Design

## Slide 61
Luminaire Type: Thorlux Lighting - KE18968 Kanby EVO - Low Glare.
Company name: thorlux
Lamp luminous flux = 3860 lumen.
Power=29 watt.
Luminous efficacy: 133.1 lm/w.
Colorimetric data: CCT 4000 K, CRI 80.
Used in Classrooms and Cafeteria.
Electrical Design

## Slide 62
  Luminaire Type: Thorlux Lighting – EKB10833 Kanby T5 Reflector.
  Company name : Thorlux.
  Lamp luminous flux = 2505lumen.
  Power=61 watt.
  Luminous efficacy: 41.1 lm/w.
  Colorimetric data : CCT 3500 K, CRI 80.
Used in Teachers Room and Computer Laboratory.
Electrical Design

## Slide 63: Electrical Design
Artificial Lighting Design:
Classroom
Headmaster Office
Computer Laboratory

## Slide 64: Electrical Design
Artificial Lighting Design:
Cafeteria
Library
Teachers Room

## Slide 65
Luminaires Distribution:
Electrical Design

## Slide 66
* Ceiling –mount Speakers F-101C/M from TOA company
* Coverage Angle 120º H x 120º V
Sound reinforcement system:
Electrical Design

## Slide 67
Sound reinforcement system:
Coverage area of the loudspeakers in the classrooms
Loudspeakers distribution in the ground floor
Electrical Design

## Slide 68: Electrical Design
Electrical Distribution Board for the First Floor:

## Slide 69: Mechanical Design
Firefighting
HVAC
Water Drainage
Water Supply

## Slide 70: Mechanical Design
Water Supply System:
Capacity of Water Tank = 12
Pipe | Diameter(inch)
Vertical Diameter | 2
Horizontal | 1 1/2
Branch | 1

## Slide 71: Mechanical Design
Water Drainage System:

## Slide 72: Mechanical Design
Storm Water:
Capacity of Storm Water Tank = 1010

## Slide 73: Mechanical Design
HVAC System:
HVAC System for the Multipurpose Room
Mechanical Ventilation in the W.C’s

## Slide 74: Mechanical Design
Safety System
Firefighting System:

## Slide 75: Mechanical Design
Safety System
Detection and Notification System:

## Slide 76
Flame Detector
Smoke Detector
Mechanical Design
Safety System
Detection and Notification System:

## Slide 77: Mechanical Design
Safety System
Exit Routes:
Emergency Exit Sign

## Slide 78: Environmental Design
Daylighting
* Daylighting Factor
* Sun path analysis
Thermal Design
Acoustical Design

## Slide 79: Daylighting in school floors:
Environmental Design
Daylighting Design:

## Slide 80: Daylighting factor for school spaces:
Zone | Actual DF% | Standard DF% | Comply/Not
Classrooms | 2.3 | (1.5-2.5) | Comply
Offices | 2.00 | (1.5-2.5) | Comply
Cafeteria | 3.6 | (2.5-4) | Comply
Laboratory | 2.75 | (2.5-4) | Comply
Environmental Design
Daylighting Design:

## Slide 81: Acoustical Design:
RT 60 and
Environmental Design

## Slide 82: RT 60 for class rooms and offices:
Environmental Design
Acoustical Design:

## Slide 83: Noise Control:
Component | STC (dB) | Standard
External Walls | 51 | 40-55
Partitions | 34 | 40-55
Environmental Design
Acoustical Design:

## Slide 84: Noise Control:
Component | IIC (dB) | Standard
Celling | 57 | <57
Environmental Design
Acoustical Design:

## Slide 85
External Wall Layers
Block–Partition Layers
Environmental Design
Layers of Structural Elements:
Thermal Design:
Roof Layers

## Slide 86: Thermal Design:
Temperatures:
Air temperatures: 20 c
Radiant temperature: 18.23c
Operative Temperature: 19.11c
Relative Humidity : 61:0%
Environmental Design

## Slide 87: Environmental Design
Thermal Design:
Total Heating Load = 215.4 kW
Total Cooling Load = 43.7 kW

## Slide 88: Comfort curves:
Temperature
RH
PMV
Environmental Design
Thermal Design:

## Slide 89: Environmental Design
Sun path Diagram:
21-july at 8:00

## Slide 90: Environmental Design Sun path Diagram

## Slide 91: Energy consumption =129.48 kw.hr/m
Environmental Design
Thermal Design:

## Slide 92
Item | Total cost (NIS)
Earth work | 467,358.4
Structural work | 2,500,000
Architectural Finishes | 2,622,297
Electrical work | 57,308
Mechanical work | 297,690
Total cost of building | 5,915,564
The total cost of the project equals 5.915,564 NIS
(1,183,131 JD)
The unit cost equals 1355.50 NIS/m2
271.10 JD/m2
Quantity Surveying