## Slide 1
An-Najah National University
Faculty of Engineering
Civil Engineering Department
Structural analysis and design of Dr. Ziad Sinan mall-Jenin
Prepared By:
Osaid Ayman
Dunia Sabra
Salsabeel Hamdi
Supervisor: : Dr. Mohammad Samaaneh

## Slide 2: Outline :
Background information
Analysis and design inputs
Conceptual design
ETABs modeling & checks.
Design.

## Slide 4
Location:
The project addresses is the analysis and design of Dr. Ziad Sinan mall (7683.5 m2) located in Jenin .

## Slide 5
Basement floor

## Slide 6
Ground floor

## Slide 7
1st,2nd and 3rd floor

## Slide 8
Floor number | Function | Area (m2) | Height(m)
Basement (B1) | Parking | 1922 | 4.40
Ground floor (GF) | Shops | 1922 | 5.10
First floor (F1) | Offices&Shops | 1916.3 | 3.50
Second floor (F2) | Offices& Shops | 1923.2 | 3.50
Third floor(F3) | offices&Shops | 1923.2 | 3.50
Floors, functions areas and heights

## Slide 9
This project consists of three blocks that are shown in figure and the structural system used for whole project is two way solid slab.

## Slide 10
    Concrete:
Unit weight of reinforced concrete = 25 kN/m³
Structural element | Fc` (MPs) | Concrete type | Modulus of elasticity(MPs)
Beams, slabs , stairs | 24 | B300 | 23025
Footings, columns, shear walls | 28 | B350 | 24870
Reinforcement steel:
Yielding strength (Fy) = 420MPa.
Modulus of elasticity (Es) = 200GP
Materials:

## Slide 11: The bearing capacity of the soil in the region of the mall is estimated to be (180) kN/m2.
Soil properties:

## Slide 12
Loads :
Gravity
Lateral
Loads
Dead
Live
Earthquake

## Slide 13
  Load:
Dead Load:
13
Live load:
In this project, a live load of 4.8 kN/m2 will be used for whole structure, according to ASCE.
Slab own weight for solid= 5 KN/m2
Superimposed dead load=3.6 KN/m2
Wall load= 6.64 kN /m2

## Slide 14
    Lateral loads data:
Inputs of design | 
Site class | D
Risk category | II
Seismic force resisting frame | Special reinforced concrete shear walls
R | 6
Ss | 0.325g
S1 | 0.075g
Fa | 1.54
Fv | 2.4
Sms=Ss×Fa | 0.5005
Sm1=S1×Fv | 0.18

## Slide 15
Seismic design risk category at Sds =0.5005 | D
Seismic design risk category at Sd1=0.18 | C
The design seismic category | D
Redundancy factor (ρ) | 1.3

## Slide 16: Hazard map of Israel:

## Slide 17: Load combinations: According to the "ACI 318-2011 and ASCE7-10, the load factors that are used in the analysis and design are:
Ultimate combinations:
a) 1.4 D b) 1.2D + 1.6 L c) 1.2D+E+L d) 0.9D +E
Service combinations:
a) D +L
b) D +0.75L
c) D +0.7E
d) D +0.75L +0.75(0.7E) e) 0.6D+0.7E

## Slide 18: Computer programs:
  1) ETABS 2016: is used to analyze and design the structural elements.
  2) SAFE 2016
  3) CSiCOL 9
  4) AutoCAD: is used for plans and draw structural detailing.
  5) Other programs such as Excel and word.

## Slide 19
Preliminary design for block A:

## Slide 20
Slab :

## Slide 21
The Critical Panel (7.8m x 5.7m) as shown in the figure:

## Slide 22
The minimum thickness of the slab was calculated using “Direct Design Method ".
Check the validity of ACI Coefficients requirements:
1- There are two or more spans in each direction. (OK)
2- Spans are approximately equal. (OK)
3- Loads are uniformly distributed.
4- Panels are rectangular with L/B less than two. (OK)
5-Successive spans length C/C of supports in each direction do not differ by more than 1/3. (OK)
6-All loads are gravity with WL/WD Less than two. (OK)
The minimum slab thickness was calculated equal 0.167 m.
So use h = 0.2 m

## Slide 23
Check slab thickness for shear
Since ΦVc ˃> Vu, Slab thickness is adequate for resisting shear (OK). So there is no need for shear reinforcement.
𝛷𝑉𝑐=105.83 KN
Vu=64.62 KN

## Slide 24
2. Beam Dimensions :
Beam | Dimensions(mm2)
B1 | 350×700
B2 | 350×700
B3 | 350×700
B4 | 350×700
B5 | 350×700
B6 | 350×500
B7 | 350×500
After making checks, the final beam dimensions are shown in this table:

## Slide 25
Beams layout F1,F2 and F3

## Slide 26
3. Column Dimensions :
Critical column is shown below in figure below:

## Slide 27
By using tributary area method, we found the ultimate load on the critical columns=2898kN.
ØPn = δ×Ø (0.85𝑓𝑐 ′Ac + As×fy)
Ag = 200744.79 mm2.
Use h = 500 mm & b = 500 mm.
As = 0.01x500x500
= 2500 𝑚𝑚2.
so the columns dimensions are shown in table
Columns | Dimensions(mm2)
C1,C2 | 400×300
C3,C4,C5 | 400×400
C6 | 500×500

## Slide 28
Columns layout F1,F2 and F3

## Slide 29
SEISMIC ANALYSIS AND CHECKS FOR BLOCK A:

## Slide 30
3D modal for block A:

## Slide 31
Modifiers for structural element of block A:
Modifiers/Section | B0.35×0.7 | B0.35×0.5 | Col0.4×0.4 | Col0.5×0.5 | Col0.4×0.3 | Shear wall | Slab0.2
Cross section (axial) Area | 1 | 1 | 1 | 1 | 1 | 1 | 1
Shear Area in 2 direction | 1 | 1 | 1 | 1 | 1 | 1 | 1
Shear Area in 3 direction | 1 | 1 | 1 | 1 | 1 | 1 | 1
Torsional constant | 0.35 | 0.35 | 0.7 | 0.7 | 0.7 | 0.35 | 0.3
Moment of inertia bout 2 direction | 0.35 | 0.35 | 0.7 | 0.7 | 0.7 | 0.35 | 0.3
Moment of inertia bout 2 direction | 0.35 | 0.35 | 0.7 | 0.7 | 0.7 | 0.35 | 0.3
Mass | 1 | 1 | 1 | 1 | 1 | 1 | 1
Weight | 1 | 1 | 1 | 1 | 1 | 1 | 1
Meshing size =0.5×0.5 m2.

## Slide 32
  Block A-checks:
    Compatibility check:

## Slide 33
    Equilibrium check:
Load type | Hand results kN | ETABS results kN | Difference %
Dead | 15895.24 | 15886.8 | 0.05
SD | 4837.82 | 4835.2 | 0.05
LL | 6450.42 | 6446.9 | 0.05
wall | 2633.35 | 2631.1 | 0.085

## Slide 34
    Stress - strain check:
By using live load in this check on beam 4 span 1, so Wu=4.8𝐾𝑁/𝑚3:
MUHand =37.68 KN.m
% Difference = 1.72 % < 10 %,
so it is OK.
. Ma =-5.9 kN.m
. Mb =-24.9 kN.m
. Mc = 22.94kN.m

## Slide 35
    Deflection check:
Δlong term =25.97mm Δallawable= 32.5mm
25.97mm < 32.5 ,so it is OK.

## Slide 36
  Modal mass participation ratio:

## Slide 37
Period:
Method | Ta(sec) | Error in comparison with Method A
Method A (approximate) | 0.3995 | -
Method B (Rayleigh) | 0.435845 | 8.33% < 30%
Period for mode 1 from ETABS | 0.47 | Is less than 1.3Tn method A

## Slide 38
      Response spectrum curve:
In (sec) | inputs
0.5005 | SDS
0.18 | SD1
0.3995 | T
0.072 | To
0.36 | TS
8 | TL

## Slide 39
Base Shear:
        ETABS result for base shear (ELF) in X &Y direction :
Hand results for base shear =1873.425kN
The errors =1% less than the allowable (15%) so it is Ok.

## Slide 40
        ETABS result for base shear (Response) in X-direction :
So to reach 0.85 of ELF-X it was multiplied with scale factor.

## Slide 41
Base shear due to Response-X after multiplying with scaling factor
Scale Factor=
=
=2744.56

## Slide 42
        ETABS result for base shear (Response) in Y-direction :
So to reach 0.85 of ELF-Y it was multiplied with scale factor.

## Slide 43
Base shear due to Response-Y after multiplying with scaling factor
Scale Factor=
=
=1872.3

## Slide 44
Drift:
Drift in X-Direction
All values of drift are less than 0.02hx, so it is OK.
Floor | Drift
F3 | 0.000674
F2 | 0.000677
F1 | 0.000521
G | 0.000028

## Slide 45
Drift in Y-Direction
Floor | Drift
F3 | 0.000263
F2 | 0.000267
F1 | 0.000089
G | 0.00000
All values of drift are less than 0.02hx, so it is OK

## Slide 46
Irregularity Checks:
Horizontal Irregularity
Torsional irregularity
Floor | U1 | U2 | Δ1 | Δ2 | Δ avg | Ratio
F3 | 7.451 | 4.853 | 2.34 | 1.502 | 1.921 | 1.218116(4)
F2 | 5.111 | 3.351 | 2.316 | 1.523 | 1.9195 | 1.206564
F1 | 2.795 | 1.828 | 2.672 | 1.736 | 2.204 | 1.212341
G | 0.123 | 0.092 | 0.123 | 0.092 | 0.1075 | 1.144186
All ratios around ≈1.2 , So there is no torsional irregularity
Torsional horizontal irregularity check in X-Direction.

## Slide 47
Floor | U1 | U2 | Δ1 | Δ2 | Δ avg | Ratio
F3 | 3.336 | 2.534 | 0.917 | 0.599 | 0.758 | 1.209763
F2 | 2.419 | 1.935 | 0.93 | 0.654 | 0.792 | 1.174242
F1 | 1.489 | 1.281 | 1.124 | 0.894 | 1.009 | 1.113974
G | 0.365 | 0.387 | 0.365 | 0.387 | 0.376 | 1.029255
Torsional horizontal irregularity check in Y-Direction.
All ratios around ≈1.2 , So there is no torsional irregularity

## Slide 48
Re-entrant corners | does not exist
Diaphragm discontinuity | does not exist
Out –of-plane offsets | does not exist
Nonparallel systems | does not exist
Horizontal Irregularity

## Slide 49
Vertical Irregularity
Stiffness irregularity –soft story | does not exist
Weight (mass) irregularity | does not exist
Vertical geometry irregularity | does not exist
In-plane discontinuity in vertical lateral –force-resisting element | does not exist
Discontinuity in capacity –weak story | does not exist

## Slide 50
Foundation:

## Slide 51: In our project we have mat footing and we design it by safe program.

## Slide 52: In our project we used mat footing and it is designed using safe program. Do we really need a mat? If the ratio Area of footing >= 55% Area of building , mat is needed
After check the area of footing needed for the structure by dividing the total envelope service earth quick by soil capacity which equal =224.836 m2
Area of footing to area of basement ratio =0.623
Which is greater than 0.55 of basement area so the type of footing will be mat foundation.
The total area of mat foundation =378.6m2

## Slide 53
Checks of mat foundation

## Slide 54: Bearing capacity of soil: The maximum soil pressure is less than 180 so it is OK

## Slide 55: Deflection check: The allowable relative deflection is less than 10 mm so this check is OK.

## Slide 56: Shear capacity check(punching): the maximum ratio is less than 1 so the dimension of mat foundation is ok.

## Slide 57
SEISMIC DESIGN

## Slide 58
Slab design:
Shear:

## Slide 59
Flexure:

## Slide 62
Beams reinforcement:
Group | SPAN | A | C | E | F | G | Al in the middle of the beam | S1 | S2 | Stirrups
B1 | 1 | 5Ø20 | - | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 20cm | 1 Ø10
 | 2 | - | 6Ø20 | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 20cm | 1 Ø10
 | 3 | 6Ø20 | 6Ø20 | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 20cm | 1 Ø10
B2 | 1 | 4Ø20 | - | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 2 | - | 6Ø20 | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 3 | 6Ø20 | 6Ø20 | 3Ø20 | 4Ø20 | 2 | 2 Ø12 | 10cm | 25cm | 1 Ø10
B3 | 1 | 4Ø20 | 4Ø20 | 4Ø20 | 4Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
B4 | 1 | 3Ø20 | - | 2Ø20 | 3Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 2 | - | 3Ø20 | 2Ø20 | 3Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 3 | 3Ø20 | 3Ø20 | 2Ø20 | 3Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
B5 | 1 | 3Ø20 | - | 2Ø20 | 4Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 2 | - | 5Ø20 | 5Ø20 | 4Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 3 | - | 5Ø20 | 5Ø20 | 4Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
 | 4 | 3Ø20 | 3Ø20 | 2Ø20 | 3Ø20 | - | 2 Ø12 | 10cm | 25cm | 1 Ø10
B6 | 1 | 3Ø20 | 3Ø20 | 2Ø20 | 3Ø18 | - | 2 Ø12 | 10cm | 20cm | 1 Ø10
B7 | 1 | 5Ø20 | - | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 20cm | 1 Ø10
 | 2 | - | 6Ø20 | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 20cm | 1 Ø10
 | 3 | 6Ø20 | 6Ø20 | 3Ø20 | 3Ø20 | 2 | 2 Ø12 | 10cm | 20cm | 1 Ø10

## Slide 63
Beams layout F1,F2 and F3

## Slide 66
Columns reinforcement:
Group No. | Floor No. | Dimension mm2 | Height m | No. of bars | S0 | S1 | Ties
C1 | G | 400×300 | 4.4 | 10Ø18 | 100 | 100 | 1 Ø 10
 | F1 | 400×300 | 5.1 | 10Ø18 | 100 | 100 | 1 Ø 10
 | F2 | 400×300 | 3.5 | 10Ø18 | 100 | 100 | 1 Ø 10
 | F3 | 400×300 | 3.5 | 10Ø18 | 100 | 100 | 1 Ø 10
C2 | G | 400×300 | 4.4 | 10Ø14 | 100 | 100 | 1 Ø 10
 | F1 | 400×300 | 5.1 | 10Ø14 | 100 | 100 | 1 Ø 10
 | F2 | 400×300 | 3.5 | 10Ø14 | 100 | 100 | 1 Ø 10
 | F3 | 400×300 | 3.5 | 10Ø14 | 100 | 100 | 1 Ø 10
C3 | G | 400×400 | 4.4 | 12Ø16 | 100 | 100 | 1 Ø 10
 | F1 | 400×400 | 5.1 | 12Ø16 | 100 | 100 | 1 Ø 10
 | F2 | 400×400 | 3.5 | 12Ø16 | 100 | 100 | 1 Ø 10
 | F3 | 400×400 | 3.5 | 12Ø16 | 100 | 100 | 1 Ø 10
C4 | G | 400×400 | 4.4 | 12Ø22 | 100 | 100 | 1 Ø 10
 | F1 | 400×400 | 5.1 | 12Ø22 | 100 | 100 | 1 Ø 10
 | F2 | 400×400 | 3.5 | 12Ø22 | 100 | 100 | 1 Ø 10
 | F3 | 400×400 | 3.5 | 12Ø22 | 100 | 100 | 1 Ø 10
C5 | G | 400×400 | 4.4 | 12Ø14 | 100 | 100 | 1 Ø 10
 | F1 | 400×400 | 5.1 | 12Ø14 | 100 | 100 | 1 Ø 10
 | F2 | 400×400 | 3.5 | 12Ø14 | 100 | 100 | 1 Ø 10
 | F3 | 400×400 | 3.5 | 12Ø14 | 100 | 100 | 1 Ø 10
C6 | G | 500×500 | 4.4 | 12Ø16 | 100 | 100 | 1 Ø 10
 | F1 | 500×500 | 5.1 | 12Ø16 | 100 | 100 | 1 Ø 10
 | F2 | 500×500 | 3.5 | 12Ø16 | 100 | 100 | 1 Ø 10
 | F3 | 500×500 | 3.5 | 12Ø16 | 100 | 100 | 1 Ø 10

## Slide 67
The key of columns:

## Slide 73
Shear wall reinforcement:

## Slide 75
Mat reinforcement:
Moment m11 top in X-direction
Fig. ‎6.29 M22 top in Y-direction.

## Slide 76
Moment m11 bottom in Y-direction.
Moment m22 bottom in x-direction

## Slide 79
Stairs reinforcement:

## Slide 81
Thank You ^^