## Slide 1: An-Najah National University Faculty of Engineering Civil Engineering Department GRADUATION PROJECT II 3D Analysis and Design of WebTech Company Building With Supplementary Steel Frame
Supervisor : Dr. Monther Diab

## Slide 2: Prepared by:
Ahmad Ghassan Mubarak
Jamal Samer Harb
Omar Samer Shaheen

## Slide 3: Outline : PART 1 (CONTINUED)
Chapter 5: Dynamic Analysis and Static Check
5.1 Calculation of Center of Rigidity and Center of Mass
5.2 Static Analysis
5.3 Dynamic Analysis
Chapter 6: Analysis and Design Of Foundations
6.1 Design of Strip Footing
6.2 Design of Combined Footing
6.3 Design of Isolated Footing
6.4 Design of Tie Beam
Chapter 7: Design of Helical Stair

## Slide 4: Outline : PART 2
Static Analysis and Design of Steel Frame Structure
{ SUPPLEMENT STORAGE BUILDING }
Chapter 1: Introduction
1.1 Project Description
1.2 Location and Function
1.3 Site and Geology
1.4 Design Codes
1.5 Materials
1.6 Basic Date Used for Design
1.7 Layout and Elevation of the Structure

## Slide 5: Outline : PART 2
Chapter 2: Checks and Verification of 3D SAP Model
2.1 introduction
2.2 Compatibility Check
2.3 Equilibrium Check
2.4 Stress Strain Relationships

## Slide 6
Chapter 3: Static Design and Check of Structure
3.1 Introduction
3.2 Check Serviceability of Structure
3.3 Design of Purlins
3.4 Design of the Rafter Beam
3.5 Design of the Columns
3.6 Design of Bracing System:
3.7 Design of the Connections
3.8 Design of the Base Plate
3.9 Design of Foundation Underneath Base Plate
Outline : PART 2

## Slide 7: Introduction
A company branch building that consists of 5 stories, with an area of 1741.2 m2/story, in addition to a parking lot, Located at “Al-Toor “ in Jarzeem mountain in Nablus city.
The building will be built on rock soil that has a bearing capacity of 400 KN/m2.
The structural system of the building will be traditional system that consists of frames .
The building is designed as two way solid slab with drop beams.

## Slide 8: Design Determinants
Materials
Structural Materials
Concrete
For slabs and beams, concrete compressive strength f’c = 28 MPa.
For columns and footings, f’c = 30 MPa.
Unit weight of reinforced concrete = 25 KN/m3.
Reinforcing steel
Steel is Grad 60 with steel yielding strength Fy = 420 MPa.

## Slide 9: Design Determinants
Non-structural Materials
Material | Unit Weight KN/m3 .
Plain Concrete (Mortar) | 23
Filler | 18
Polystyrene | 0.3
Blocks | 12
Tiles | 22
Masonry stone | 27
Glass | 25

## Slide 10: Design Determinants
Loads
Dead loads : Static permanent loads composed from the weight of structural elements as well as partitions ( Superimposed) .
Superimposed dead load = 4.2 KN/m2
Live Load : is the load produced by the use and occupancy of the structure,
for Office buildings, uniformly distributed live load 50psf ( 2.5 KN/m2 )
which has been stated using IBC Code / Table 1607.1

## Slide 11: Design Determinants
Concrete Design Codes
The American Concrete Institute Code (ACI 318-08).
International Building Code (IBC 2009).

## Slide 12: Center of Mass , Center of Rigidity
Center of Rigidity = ∑ (K d)/ ∑K
Center of Mass using centroid equation = ∑ (Ad)/ ∑A
Hand calculation of CR : X = 22.64117 , Y = 23.04124
Shear wall | Ix | Iy | x | y | X x Ix | Y x Iy
1 | 4.1438 | 4.143818 | 0.8984 | 44.784 | 3.7228 | 185.58
2 | 9.7168 | 11.15071 | 1.39 | 2.3567 | 13.506 | 26.279
3 | 11.151 | 9.716808 | 43.326 | 44.293 | 483.12 | 430.38
4 | 0.8694 | 0.856714 | 26.985 | 26.611 | 23.461 | 22.798
5 | 0.8637 | 0.867348 | 19.059 | 18.69 | 16.461 | 16.211
6 | 14.879 | 14.8865 | 27.027 | 18.659 | 402.13 | 277.77
Total | 41.623 | 41.62189 |  |  | 942.4 | 959.02

## Slide 13
Center of mass using Autocad: X = 20.5672 , Y = 25.1157
Etabs result of CM and CR :
Error in CM is small and differences in CR due to hand calculation based on rigidity of shear wall only
The differences in Center of Rigidity is less than 10% , (Acceptable)
Story | XCM | YCM | XCR | YCR
 | m | m | m | m
Story1 | 19.6863 | 25.9923 | 19.5819 | 26.0627
Story2 | 19.601 | 26.0773 | 21.0961 | 24.6603
Story3 | 19.6864 | 25.9924 | 21.9285 | 23.9117
Story4 | 19.6862 | 25.9923 | 22.3428 | 23.5578
Story5 | 19.6008 | 26.0777 | 22.5656 | 23.374
Story6 | 19.7258 | 25.9539 | 22.7095 | 23.2495

## Slide 14
Differences in center of rigidity between stories due to torsional twist of the story Combined with the transitional displacement
Reduced by reducing the deference between CM and CR
Torsion effect on stiffness center from Eurocode 8 the smallest of :

## Slide 15
Combination of transitional and twist movement :

## Slide 16: Equivalent Static Method :
According to method B UBC97 Section 1630.2.2
Period = 1.3 sec
For Nablus we take zone 2B for seismic acceleration
Solid Profile: SB
Ductility factor R = 4.5 as we have bearing shear wall
Load Pattern | Hand Calculation
Live Load | 25226.33
Superimposed | 52338.48
Dead Load | 99774.47

## Slide 17
Base Shear UBC97 Section 1630.2.1
Cs= (Cv x I)/(R x T)
V= Cs x W = 5416 KN
For Weight we take W= DL+SD+ 0.25L = 158419.5 KN
Etabs Result: W= 161414.64
Base Shear V = 5521 KN The value is accepted since the error =1%

## Slide 18: Dynamic Analysis Using Response Spectrum:
According to UBC97 we have to take horizontal load cases as the following
Ehx = Ex + 0.3 Ey
Ehy = Ey + 0.3 Ex
A factor of gI/R must be multiplied to the Response Spectrum Function
Priliminary factor used = 2.18
Base shear = 4464 KN less than static base shear (5521 KN )

## Slide 19
According to UBC97 Section 1631.5.4
Increase factor by (5521/4464 ) = 1.23
Result static base shear = dynamic

## Slide 20: Chapter 6: Analysis and Design of Footings
Design of isolated footing
Column dimensions 80x80 cm
Service load = 7533 kN
Ultimate load = 9540 kN
Soil bearing capacity = 400 kPa
Area of footing = = 18.83 m2
Since the footing is square, a 4.4-m footing is used

## Slide 21
Thickness Determination
Based on wide beam shear
Vu = 493 (1.8 - )
ØVc = 0.75 × × × 1000 × d / 1000
Vu = ØVc -------> d = 753.53 mm.
Take d = 760 mm ------> h = 850 mm.

## Slide 22
Check for punching shear
ØVc = 0.75 × × × 6240 × 760 / 1000 = 6494 kN.
Vu = 9540 – 493 × 6.240 ×0.760 = 7202 kN > ØVc
Using an approximate formula
d = 10 = 977 mm, say 1000 mm.
h = 1100 mm.

## Slide 23
Design for flexure
Mu = = 798.7 kN.m/m
ρ = 0.00215 /m
As = 2150 mm2/m
As,min = 0.0018 × 1000 × 1100 = 1980 mm2/m < As
Use 5Ø24 /m both directions

## Slide 24: ISOLATED FOOTING DIMENSIONS & REINFORCEMENT DETAILS

## Slide 25: Design of Tie Beam
Tie Beam: Max load 8782 KN.
10% x 8782 = 878 KN tension
T = Fy As
878/(420*10^3) = 0.00209 m2 steel = 2091 mm2 steel
Use 1% as steel ratio
Area of concrete = 2091/0.01 = 209095 mm2
Use section 40 x 60 width (Area = 2400 cm2)
For all tie beam use steel 10Y18 steel 5 bars top 5 bars bottom

## Slide 26: SCHEDULE OF TIE BEAM SECTION &R.F.T DETAILS

## Slide 27: Design of Helical Stair
The following is the detailing of Helical Stair of 1.5 m width and 4.0 m height.

## Slide 28: Design of Helical Stair: Cross Section

## Slide 29
PART II
Static Analysis and Design of Steel Frame Structure
{ SUPPLEMENT STORAGE BUILDING }

## Slide 30: Chapter 1: Introduction
Project Description
This part of the project is a structural analysis and design of supplement steel storage frame for WebTech company branch at Nablus city, the design consists of steel frame, bracings and interlocking systems.
1.4 Design Codes
In this project, the following codes will be used:
Steel Design Specifications and Code ( AISC 2005 )
Loads are calculated according to Egyptian Code for Loads (EPC 2012)
Palestinian Central Bureau of Statistics (PCBS)

## Slide 31
Basic Data Used for Design
The structure is assumed to be in Nablus\ Al_Toor.
Steel used in design is mild steel (A36_Steel).
Concrete compressive strength for foundation f’c = 30MPa.
Assume using A325 Bolts (Fu = 827MPa) for connections.
Threaded rods for base connections according to ASTM A354 Grade BD.
Any other assumptions will be clarified through design.

## Slide 32
Layout and Elevation of the Structure

## Slide 33: Chapter 2: Checks and Verification of 3D SAP Model
Compatibility Check
Compatibility has been checked as shown in figure, and it seems that the modeling is ok.

## Slide 34
Equilibrium Check
Sum of sections weight = 83430.67 Kg → 834.31 KN.
SAP result = 846.46 KN.
Percent of error = x 100% = 1.43% (Acceptable)
Section Type | Weight (Kg\m) | Length (m) | Number | Total weight (Kg)
HE 600 x 151 | 151 | 9.6 | 16 | 23193.6
HE 300 A | 88.3 | 7.5 | 24 | 15894.0
IPE 400 O | 75.7 | 10.05 | 18 | 13694.13
IPE 270 | 36.1 | 6.0 | 16 | 3465.6
L 203 x 203 x 19 | 57.9 | 7.2 | 16 | 6679.34
UKPFC 300 x 100 x 46 | 45.5 | 6 | 64 | 17472.0
UPN 260 | 37.9 | 5 | 16 | 3032.0

## Slide 35
For live load
Live load on the surface area = 0.5 x 964.8 = 482.4 KN.
SAP result = 842.39 KN.
Percent of error = 0% (Very Good)
For Covering load
Weight of the covering over the area = 0.15 x 964.8 = 144.72 KN.
SAP results = 144.718 KN.
Percent of error = 0% (Very Good)
For wind load (Case1)
In Z direction = { 0.545 x 10.05 x 48 } + { 0.3403 x 10.05 x 48 } = 427.068 KN.
SAP result = 424.944 KN.
Percent of error = x 100% = 0.49% (Acceptable)

## Slide 36
In X direction = { 0.545 + 0.3403 } x 7.5 x 48 = 318.7 KN.
SAP result = 326.688 KN.
Percent of error = x 100% = 2.5% (Acceptable)
For Wind load (Case2)
In Z direction = { 0.3403 x 10.05 x 48 } x 2 = 328.32 KN.
SAP result = 326.688 KN.
Percent of error = x 100% = 0.49% (Acceptable)
In X direction = { 0.4765 x 100 } + { 0.3403 x 100 } = 81.68 KN.
SAP result = 81.68 KN.
Percent of error = 0% (Very Good)
Equilibrium Satisfied

## Slide 38
2.4 Stress Strain Relationships
This test should be conduct to ensure that SAP Stress-Moment results are trusted.
Check the moment on Purlin
Weight of the Purlin = 6 x 45.5 x 10 x 10-3 = 2.73 KN\m.
Weight of the covering on Purlin = 0.15 x 2 = 0.3 KN\m.
Weight of live load on Purlin = 0.5 x 2 = 1 KN\m.
W max = 1.2 { 0.455 + 0.30 } + 1.6 {1} = 2.5 KN\m.
Ultimate moment = = = 11.27 KN.m
SAP result = 12.07 KN.m
Percent of error = 6.62% (Acceptable)

## Slide 39: Chapter 3: Static Design Check of Structure
Loads
For superimposed dead load (Covering), sandwitch panel of 15 Kg\m2, i.e (0.15KN\m2).
According to table 4.1 in EPC 2012, live load can be taken 0.5 KN\m2 for inclined surfaces.
Calculation of wind load
q = 0.5 (1.25)(33)2(1.0)(1.0) = 680 .6 N\m2
Here we have two cases:
Case 1: Pressure on exterior surfaces when the wind comes from side of the structure
Case 2: Pressure on exterior surfaces when the wind comes from front of the structure

## Slide 40
Wind Effect Case 1:

## Slide 41
Wind effect Case 2:

## Slide 42: Check Serviceability of Structure
Deflection due to live load = 39.75 mm < = =83.33 mm. (Satisfied)
Deflection due to dead load + live load = 82.21 mm< = =111.11 mm. (Satisfied)
Deflection due to wind load (Case1) = 35.32 mm < = =111.11 mm. (Satisfied)
Deflection due to wind load (Case2) = 30.57 mm < = =111.11 mm. (Satisfied)

## Slide 43
Design of the Rafter Beam
Max bending moment and shear force = 238.036 KN.m & 75.5 KN
Max axial load: 43.67 KN.
As a previous estimation, select a section that satisfy the following < Fu
< 400 → Z = 595 x 103 mm3. Try a section that has largest plastic modulus.
Z = {{180x13.5x193.4} + {8.6x186.5x93.25}}x2
Z = 1239051.35 mm3 > 595000 mm3 OK
Select section IPE 400

## Slide 44: Check the adequacy of the previous section
Check the capacity of the section for bending moment
Unbraced length of the compression flange = 10.05 m.
Limiting lengths Lr and Lp are calculated as specified in CHAPER F_Section F2
Lp = 1.76 ry = 1.76 (3.95)(10) = 1974.23 mm.
rts = = = 46.74
Lb = 10050 mm → (Lp < Lb < Lr) → ZONE II → Inelastic LTB
Moment Capacity of the section is calculate according to the equation

## Slide 45
Cb = 1.248
Mp = Zx Fy =1239051.32 x 248 x 10-6 = 307.28 KN.m
Mr = Sx (0.7Fy) = 1160 x 103 (0.7)(248)10-6 = 201.37 KN.m
Mn = 1.248 {307.28 – (307.28 – 201.37) () } = 382.35 KN.m > Mp Take Mn=Mp
For design, ø Mn = 0.9 x 307.28 = 276.55 KN.m > Mu OK
Check stresses on the section , According to AISC2005 _ Table B4.1
ʎ p = 0.38 = 0.38 = 10.8
ʎ r = 1.0 = 1.0 = 28.4
For flange with < ʎ p → Flange is Compact
Check webs due to bending
ʎ p = 3.76 = 3.76 = 106.77
ʎ r = 5.7 = 5.7 = 161.87
For web with < ʎ p → Web is Compact
The whole section regarding to LTB is compact.

## Slide 46
Check minimum length of the member in tension
ʎ = ≤ 300 → = 254.43 ≤ 300 OK
Check yielding of the member due to tension
Ø Pn = ø Ag Fy = 0.9 (8450)(248)(10-3) = 1886.04 KN.
Ø Pn > Pu SAFE
Check the member for shear
Cv = 1.0
Vn = 0.6 x 248 x 10-3 x 3440 x 1.0 = 511.84 KN.
For design øVn = 1.0 x 511.84 = 511.84 KN.
øVn > Vu SAFE
IPE 400 satisfy the design criteria

## Slide 47
Design of the Columns
According to AISC (CHAPTER H, page 70), should be limited by equations H1-1a, or H1-1b.
First, you need to calculate critical , this value should be calculated for sway and
non - sway cases, then we will select the critical one. it will be obtained using Alignment charts
Sway case = = 180 (Critical)
Fcr = 0.877 Fe , Where Fe = = = 60.92MPa.
Fcr = 0.877 x 60.92 = 53.43 MPa.
øPn = ø Ag Fcr = 0.9 (97.3 x 100)(53.43)(10-3) = 467.88 KN.
= = 0.143 < 0.2, Use equation (H1-1b)

## Slide 48
For Sway Case
Calculate ø Mn for section HE 280A,
Lp < Lp < Lr → Inelastic LTB
Mn = 2.189 {261.53 – (261.53 – 175.33) } = 412.58 KN.m
Mn > Mp → Take Mn = Mp
For design øMn = 0.9 x 261.53 = 235.4 KN.m > Mu SAFE
Mux ( Ultimate moment around x-axis), Mux = B1 Mut + B2 Mlt
Mux = B1 Mut = 1.0 x 152.23 = 152.23 KN.m
Substitute at equation H1-1b, implies
+ = 0.72 < 1.0 OK, SATISFY THE EQUATION

## Slide 49
For Sway Case
Using the same equation for < 0.2
Mux = B1 Mnt + B2 Mlt
Mux = (1)(119.55) + (1.012)(71.078) = 191.47 KN.m
Substitute at equation H1-1b, implies
+ = 0.88 < 1.0 OK, SATISFY THE EQUATION
Column strength is enough for axial load.
Check the compactness of the cross section, According to AISC, Table B4.1 Case3
ʎp = NA ʎr = 0.56 = 0.56 = 15.9, < 15.9 Flange is compact.
ʎp = NA ʎr = 5.7 = 5.7 = 161.86 , < 161.86 Web is compact
The whole section regarding to LTB is Compact

## Slide 50
Check shear capacity of the section
= 33.75 < 1.10 (Case 1)
Vn = 0.6 (248)(10-3)(2160)(1.0) = 321.4 KN → For design øVn = 321.4 KN > Vu SAFE
Design of the Connections
APEX Connection, It is the connection between rafter beams.
M: 214.5 KN.m, V: 16.5 KN., A: 15 KN.
In the design of this connection, the following assumptions are encountered:
Assume bolts are A325, Fu = 827 MPa.
The bolts used are X-Type, fv = 0.5 Fu.
Weld used is E70 XX, Fu = 482 MPa.
Assume bolts diameter = 30 mm.

## Slide 51
Specify the arrangement of the bolts according to AISC requirements
According to AISC, section J3.3 (Minimum Spacing)
Bolts are subjected to shear and moment, so that
connection will be designed as a moment resisting
connection.
Direct shear (Single Shear): Fy = = = 2.06 KN.
Check shear capacity, Rn = (Ab fv) n
øPn = (0.75)(706.85)(414)(8)(10-3) = 1755.83 KN.
Check bearing of the plate (Assume deformation is a design criteria):
Rn = 1.2(29.2)(30)(400)(10-3) ≤ 2.4(30)(30)(400)(10-3) = 420.48 KN ≤ 864 KN. OK
For design øRn = 0.75 (420.48)(8) = 2522.88 KN.
øPn < øRn (Shear is controlling the design)
øPn > Pu SAFE

## Slide 52
Fz (Due to axial force) = 1.87 KN.
This is the value of axial due to direct axial force, there is another component resulted from moment around the X-axis.
Fmxz = , Where, Mx = 214.5 KN.m
Total axial force = 1.87 + 231.74 = 233.62 KN.
øRn = 0.75 Fnt Ab = 0.75 (0.75 x 827)(10-3) = 328.82 KN → øRn > Pu SAFE
You have to account for the combined effect of shear and tension
= 1.3(0.75 x 827) - x 2.917 = 800.5 MPa.
= 800.5 > Fnt ( Take Fnt’ = Fnt = 620.25 MPa)
For design øFnt’ = 0.75 (620.25) = 465.18 MPa.
Direct tension stress Ft = = 41.31 MPa.
Since øFnt’ > Ft SAFE

## Slide 53
Check the weld between the beam and steel plate
Check capacity of the weld (E70 xx) for shear:
According to AISC, for case with both longitudinal and
transverse weld, each of them is calculated separately:
For longitudinal weld ( Web beam weld ):
RnL = Fw Aw = 0.6(482)(0.707 x 3)(524.18)(10-3) = 321.5 KN.
For transverse weld (Beam flange weld ):
Rnt = (0.6 FEXX)(1 + 0.5 sin 1.5)Aw = (0.6 x 482)( 1 + 0.5 sin1.590)(0.707 x 8)(702.8)(10-3)
Rnt = 1724.37 KN.
According to AISC, the nominal strength of the weld is the larger of
Rn = RnL + Rnt = 321.5+ 1724.37 = 2045.87 KN.
Rn =0.85 RnL + 1.5 Rnt = (0.85)(321.5) + (1.5)(1724.7) = 2860.32 KN. (Larger).
Rn = 2860.32 KN.
For design øRn = 0.75 (2860.32) = 2145.24 KN > Vu SAFE

## Slide 54
The following shows the detailing and solid work simulation for APEX Connection

## Slide 55
Beam to Column Connection, It’s the connection between column and rafter beam.
It was also designed in the same way
The following are the details

## Slide 56
Design of the Base Plate
Column is HE 280A
Take the Ultimate Factored Load in all base plates at which it will design for.
Fz = 421.00 KN.
Fy = 163.20 KN.
Fx = -39.54 KN.
Mx = 66.50 KN.m
My = -147.40 KN.
Assuming that Base Plate covers a part of area of the footing:

## Slide 57
Take Pp = 1.7 f’c A1 → 421.00 x 103 = 0.6(1.7)(25)(A1) Solve for A1 = 16509.8 mm2.
A1 = B x L → (2 n + 0.95 D) (2 n + 0.8 Bf) = 16509.8
Solving for n = 60.8 mm.
B = 2(60.8) + 244 = 356.6, Try 370mm.
L = 2(60.8) + 256.5 = 378.1, Try 380mm.
To find the thickness of the plate
T = l , where l is the max of (m or n)
m = = = 61.75
n = = = 73.00 MAX
T = 73.00 = 11.95 mm USE 12 mm.

## Slide 58
Design of Foundation Underneath Base Plate
Dead load = 110.5 KN , MD = 8.3 KN.m
Covering = 35.2 KN , MC = 2.82 KN.m
Live load = 117.38 KN , ML = 9.4 KN.m
Area dimensions = 1.2 m x 0.85 m .
Take d = 250 mm, h = 300 mm.
Check Punching Shear
Vu = 481.74 x 1.2 x 0.85 = 491.37 KN.
øVc = 0.75 x 0.333 x x d bo = 0.75 x 0.333 x x 250 x 2500 x 10-3 = 855.8 KN.
øVc > Vu SAFE

## Slide 59
Check Wide Beam Shear
Vu = 481.74 x 0.16 = 77.07 KN.
øVc = 0.75 x (1/6) x x 1000 x 250 x 10-3 = 171.16 KN\m
øVc > Vu SAFE
Reinforcement
For long direction
Mu = = = 40.5 KN.m\m
b = 1000 mm , d = 250 mm. ρ = 1.73 x 10-3 , As = 434 mm2\m
As Min = 0.0018 bh = 540 mm2\m. As < As Min USE As Min
For short direction
Mu = 13.87 KN.m\m , As = 158 mm2 , As < As Min USE As Min

## Slide 60: Thanks for Listening