## Slide 1
HVAC SYSTEM DESIGN
Businessmen Club
The students:
Supervisor:
Dr Salameh Abdulfattah
Ameer Khaled (10716625)
Nabil abu hanih (10840770)
Saleem Sama’neh (10716714)
Tariq Ismail (10740129)

## Slide 2: The Aim of The Project
The aim of this project is to design installation of heating, ventilation and air condition system (HVAC) for buissnessmen club in ramallah .
VRV system will be used to design air conditioning.
Water service and plumping design is required for service system inside the building
Fire protection system will used in the building

## Slide 3
Presentation out line
  - Building Description.
  - Heating And Cooling loads.
  - Duct Design.
  - Plumping System .
  - Fire Fighting System.

## Slide 4
Businessmen Club
club location
City: Ramallah, Tira, Tal Es-Safa.
Elevation: 840 m above sea level.
Latitude: 32˚
Basement 2 | Pool mechanical room, electric room, kitchen, relaxing area, store, massage room, manicure pedicure room, gym.
Basement 1 | Swimming room, Jacuzzi, shower area, storage, lockers room, steam room, sauna, mechanical room.
Ground floor | Pantry, multi-purpose hall, kitchen, electric and server room, restaurant.
First floor | Open kitchen restaurant, pantry, cloak room, foyer, kitchen, lobby, lounge bar.
Building face is to the south direction

## Slide 5
Outside design condition | Inside design condition | Parameters
6 °C | 22 °C | T: temperature
65 % | 50 % | Φ : relative humidity
3.5 g of water/kg of dry air | 8.75 g of water/kg of dry air | W : moisture content
14 °C |  | Tun: unconditioned temperature
9 °C |  | Tg : ground temperature
10.8 m/s. |  | The wind speed
climate zone in winter
-Inside and out side design condition in winter (heating):

## Slide 6
1. Q = U* A* ( Ti - To )
Vvent = n * value of ventilation
Vinf = (ACH * inside volume *1000) /3600
2. Qs)vent , inf = 1.2 Vvent,inf*(Ti-To)
Ql)vent , inf = 3 Vvent,inf*(Ti-To).
3. Qbuilding = Qs)cond + Qs)v,inf + Ql)v ,inf
4. Qboiler = 1.1*Qw
The Heat load Equation :

## Slide 7
Heating load (kw) | Floor
37.86 | Basement 2
29.75 | Basement 1
42.2 | Ground
63.46 | First
164.2 | Total
Summary for heating load

## Slide 8
Outside design condition | Inside design condition | Parameters
32 °C | 23 °C | T: temperature
44% | 50 % | Φ : relative humidity
14.75 g of water/kg of dry air | 8.75 g of water/kg of dry air | W : moisture content
14 °C |  | Tun: unconditioned temperature
29°C |  | Tg : ground temperature
>5 m/s. |  | The wind speed
Inside and out side design condition in summer (cooling)
climate zone in summer

## Slide 9
Cooling Load equation :
1 ) For ceiling :
Q=U*A*(CLTD)corr (CLTD)corr = (CLTD + LM) K + (25.5 – Ti )+ (To – 29.4)
Where : K=0.5 light color
2) For walls : Q =U*A*(CLTD)corr Where : K= o.65
3)For glass : Heat transmitted through glass: Q=A*(SHG)*(SC)*(CLF) Convection heat gain: Q=U*A*(CLTD)corr

## Slide 10
Cooling Load equation :
4 ) For people: Qs= qs*n*CLF QL= qL*n
5) For lighting:
Qs= A*q*CLF 6) For equipments:
Qs= qs*CLF QL= qL

## Slide 11
Cooling load (kw) | Floor
68.1 | Basement 2
45.8 | Basement 1
88.6 | Ground
105 | First
307.5 | Total
Summary of cooling load

## Slide 12
VRV SYSTEM:

## Slide 13
Duct design:
          Design procedures:
1. The total sensible heat was calculated.
2. The Vcirculation was calculated.
3. The flow rate (CFM) was calculated.
4. Number of diffusers are calculated and distributed uniformly.
5. The initial velocity for the main duct is 5 m/s.
6. The pressure drop is depend on the initial velocity for the main duct and flow rate (CFM).
7. The main diameter is calculated.
8. The height and width of the rectangular ducts are determined from the tables.

## Slide 14
Sample Calculation For Duct Design
section | Flow ratee (CFM) | Velocity (fpm) | ∆P/L (pa/m) | D(mm) | H(mm) | W(mm)
A-B | 3200 | 1300 | 0.872 | 539.6 | 550 | 450
B-C | 1600 | 1096.5 | 0.872 | 415.5 | 400 | 350
C-D | 400 | 778.3 | 0.872 | 264.7 | 250 | 200
C-E | 1200 | 1021.8 | 0.872 | 372.7 | 300 | 400
E-F | 800 | 924.6 | 0.872 | 320.1 | 250 | 350
F-G | 400 | 778.3 | 0.872 | 264.7 | 250 | 200

## Slide 18
Plumping system
Plumping system consist of:
Potable water system.
Drainage system.
Firefighting system.

## Slide 19: Plumbing System
Total demand water :
Demand Water (L/S) | Totally Fixture Unit | Type Of Supply Water
7.41 | 360 | Cold
4.2 | 95 | Hot

## Slide 20
20
20

## Slide 22
22
22

## Slide 23: Sample of calculation for determined number of fixture unit:
Total Fixture |  |  | Quantity | Pipe Size |  | Fixture |  |  | Type
total | hot | cold |  | hot | cold | total | hot | Cold | 
30 |  | 10 | 3 |  | 1 | 10 |  | 10 | W C
6 | 5 | 5 | 3 | 3/8 | 3/8 | 2 | 1.5 | 1.5 | Lavatory
12 | 9 | 9 | 3 | 1/2 | 1/2 | 4 | 3 | 3 | shower
20 |  | 10 | 2 |  | 1 | 10 |  | 10 | urinal
68 | 14 | 34 |  |  |  |  |  |  | Total Fixture
3.6 | 1.91 | 2.75 |  |  |  |  |  |  | Total Demand ( L/S )

## Slide 24
24

## Slide 25
25

## Slide 26: Fire Fighting Design
The net area of each floor is less than 7432 m2 (80000 ft2) that means we should use one raiser only.
The building has one raiser which takes 250 GPM and has a pipe diameter of 4".
* We chose to use the standpipe system which consists of two main part:
Cabinet: Diameter of the hose = 1½ ".
Flow rate = 100 GPM.
Pressure = 65 Psi.
Land valve: Diameter = 2½ ".
Flow rate = 250 GPM.
Pressure = 100 Psi.

## Slide 27: Fire Fighting Design

## Slide 29
LAF = 19.21 m.
LFH = 0.91 m.
ΔPpump = ΔP(friction + fitting) + ΔPhead + Δpflow
ΔPfriction = (ΔP/L)AF * LAF + (ΔP/L)FH * LFH
= (1)(19.21) + (15)(.91)
= 32.86 Psi
To convert it to Pa:
ΔPfriction = (32.86)*(3.3*6.8*1000/100)
= (32.86)*(224.4)
= 7373.784 Pa
ΔP(friction + fitting) = 1.5 ΔPfriction = 1.5 *7373.784
= 11060.67 Pa.

## Slide 30
ΔPhead = Lhead *
= 12 * 9.81 *103
= 117720 Pa.
ΔPflow = 100 Psi for the landing valve.
= 100*6.8*103
= 680000 Pa.
ΔPpump = ΔP(friction + fitting) + ΔPhead + ΔPflow
= 11060.67 + 117720 +680000
= 808.780 kPa.
Tank volume = (Q*Time*3.78)/1000
= (250*2*60*3.78)/1000
= 113.4 m3/hr.