## Slide 1: Structural Aspect 04
Assumptions
Design
Structure Model
Seismic Checks
Structural Details

## Slide 2: Structural Aspect
Assumptions
American Concrete Institute ACI 318- 2014.
Uniform Building Code (UBC 97).
Minimum Design Loads for Buildings and Other Structures (ASCE 7-16).
Codes Used
General Notes
Soil used for filling | γsoil = 20KN/m3
 | Փ = 30o
N. of floors | 5
Floor Height | H = 3.5m
Concrete b400 | F’c = 32 MPa
Steel bars | Fy = 420MPa

## Slide 3: Structural Aspect
Assumptions
Loads
Seismic Factors
Load Type | KN/m2
Dead Load | As Calculated in ETAB
Super Dead Load | 5.1
Live Load | 5
Factor | Value
Seismic Zone Factor “Z” | 0.2
Importance Factor | 1
Numerical Coefficient “R” | 5.5
Soil Profile | SB
Acceleration Seismic Coefficient “Ca” | 0.2
Velocity Seismic coefficient “Cv” | 0.2
Structure Period “t” | 0.417 second

## Slide 4: Structural Aspect
Design
Columns Grid :

## Slide 5: Structural Aspect
Design
Slab System
Longest span length equal about 6.2 m.
The used structural system is one way rib slab
With 35cm thickness

## Slide 6: Structural Aspect
Design
Structural Model
Model Check
    Compatibility check

## Slide 7: Structural Aspect
Design
Model Check
    2. Deflection check
    a. Live Term Deflection Check
    The Service combination deflection. ∆ = 24.07mm
    While the Dead combination deflection.
     ∆ = 16.32mm
Longest slab length = 5.8m
Therefore the maximum allowed deflection = 5.8/360 = 16.1mm
Δlive = ΔD+L - ΔD
= 24.07 – 16.32
 7.75 mm < 16.1 mm Thus, live load deflection is acceptable.

## Slide 8: Structural Aspect
Design
Model Check
    2. Deflection check
    b. long term deflection Check
    Is the deflection came from the service load:
Longest slab length = 5.8m
Therefore the maximum allowed deflection = 5.8/240 = 24.16 mm
 24.07< Maximum allowable

## Slide 9: Structural Aspect
Design
Model Check
    3. Equilibrium check
    Columns
    Beams
    4. Stress strain check

## Slide 10: Structural Aspect
Design
Seismic Check
1. Model participant mass ratio check
Case | Mode | Period sec | Sum UX | Sum UY
Modal | 1 | 0.574 | 0.0662 | 0.4809
Modal | 2 | 0.48 | 0.1451 | 0.6683
Modal | 3 | 0.302 | 0.6251 | 0.677
Modal | 4 | 0.157 | 0.6485 | 0.779
Modal | 5 | 0.118 | 0.6573 | 0.8413
Modal | 6 | 0.098 | 0.6635 | 0.8413
Modal | 7 | 0.093 | 0.672 | 0.854
Modal | 8 | 0.089 | 0.672 | 0.8543
Modal | 9 | 0.089 | 0.672 | 0.8548
Modal | 10 | 0.082 | 0.6808 | 0.883
Modal | 11 | 0.082 | 0.8447 | 0.8841
Modal | 12 | 0.082 | 0.8453 | 0.9103
Modal | 13 | 0.082 | 0.8453 | 0.9156
Modal | 14 | 0.071 | 0.8472 | 0.9279
Modal | 15 | 0.068 | 0.8473 | 0.928
Modal | 16 | 0.066 | 0.8571 | 0.9324
Modal | 17 | 0.05 | 0.8578 | 0.9324
Modal | 18 | 0.048 | 0.8895 | 0.9388
Modal | 19 | 0.045 | 0.9066 | 0.9483

## Slide 11: Structural Aspect
Design
Seismic Check
2. Period Time check
Hand Calculated period time t = 0.417s,
while in Etab as shown in the figure t = 0.574
As method A in ubc97 code Etab should be less than 1.4 TMethod A (hand calculated period time)
T Etab < (1.4Tmethod A = 0.583s)
3. Base shear force check
Building weight | 2.5Cv | Cv/t | Manual V
27417.66 | 0.5 | 0.416 | 2077
Load Case/Combo | FX kN | FY kN | FZ kN
Dead | -2.57E-06 | 0 | 12925.83
Live | -1349.02 | -2211.94 | 6586.12
sid | -1.98E-06 | 0 | 12821.03
EQx Max | 2487.43 | 1304.62 | 1.02E-06
EQy Max | 1181.76 | 3096.66 | 1.99E-06

## Slide 12: Structural Aspect
Design
Seismic Check
4. Drift Check
Story | height | Dis X | Dis Y | Drift X | Drift Y | Delta X | Delta Y | Delta limit
Base |  | 0.00 | 0.00 |  |  |  |  | 
1.00 | 3.00 | 0.10 | 0.15 | 0.10 | 0.15 | 0.40 | 0.59 | 75.00
11.00 | 3.50 | 0.32 | 1.28 | 0.22 | 1.12 | 0.83 | 4.33 | 87.50
2.00 | 3.50 | 5.05 | 17.55 | 4.73 | 16.27 | 18.22 | 62.65 | 87.50
3.00 | 3.50 | 2.99 | 8.63 | 2.06 | 8.92 | 7.93 | 34.34 | 87.50
4.00 | 3.50 | 5.61 | 12.84 | 2.62 | 4.21 | 10.08 | 16.20 | 87.50
5.00 | 3.50 | 7.42 | 16.95 | 1.81 | 4.11 | 6.96 | 15.84 | 87.50

## Slide 13: Structural Aspect
Design
Structural details
Column
Beam

## Slide 14: Structural Aspect
Design
Structural details
Mat Footing
Slab
Ground Floor P1

## Slide 15: Structural Aspect
Design
Structural details
Slab
Ground Floor P2
First Floor

## Slide 16: Structural Aspect
Design
Structural details
Slab
Second Floor
Third Floor
Fourth Floor

## Slide 17: Accoustical Aspect 04

## Slide 18: Acoustical Aspect
Room Acoustics Design
Rooms materials as show in table
Surface | Class Room | Prayer Hall
Floor | Tiles | Moquette
Ceiling | gypsum | gypsum
Walls | plaster | plaster
Windows | glass | glass
Doors | Wood | Wood
Emergency exit Door | ---- | Steel

## Slide 19: Acoustical Aspect
Room Acoustics Design
Rooms Ease Model
Prayer Hall
Class Room

## Slide 20: Acoustical Aspect
Room Acoustics Design
Reverberation Time & Articulation Loss
Prayer Hall
The recommended RT from 1.4 to 2.6 second
With acceptable minimum value reach to 0.8 second on the required frequency.
Also The articulation loss values is less than 7% which is within the recommendation for prayer hall that shown in the sections above.

## Slide 21: Acoustical Aspect
Room Acoustics Design
Reverberation Time
Class Room
In order to reach the standard range from 0.5 to 0.9 second at 85Hz to 255Hz, panels F24 – F29 had been added.
RT Before Modification
RT After Modification

## Slide 22: Acoustical Aspect
Room Acoustics Design
Articulation Loss
Class Room
The articulation loss is less than 7% , which give
A good appreciation, as tables show.

## Slide 23: Electrical 04

## Slide 24
The suggested electrical plans.
Basement Floor
Ground Floor

## Slide 25
First Floor
Second and Third Floor

## Slide 26
the electrical current for branches will be calculated as the following equation:
The power factor equal 0.85
Then a suitable circuit beaker will be chosen
Ic.b > 1.15 load current

## Slide 27
The following table show the calculation summary for Basement floor sockets
brunch No. | No of Sockets | Power per socket | Brunch total Power | Voltage | L wire | I load (Amp) | R wire | V drop | V drop % | I C.B | I cable | Cable Area | C.B
P1 | 1 | 250 | 250 | 220 | 4.50 | 0.40 | 0.03 | 219.9 | 0.01 | 0.46 | 0.53 | 2.5 | 16
P2 | 4 | 250 | 1000 | 220 | 13.30 | 1.60 | 0.09 | 219.8 | 0.07 | 1.84 | 2.12 | 2.5 | 16
P3 | 2 | 250 | 500 | 220 | 10.30 | 0.80 | 0.07 | 219.9 | 0.03 | 0.92 | 1.06 | 2.5 | 16
P4 | 2 | 250 | 500 | 220 | 23.80 | 0.80 | 0.16 | 219.8 | 0.06 | 0.92 | 1.06 | 2.5 | 16

## Slide 28
The following table show the calculation summary for Basement floor lighting
brunch No. | total Light Power for brunch | Voltage | L wire | I load (Amp) | R wire | V drop | V drop % | I C.B | I cable | Cable Area | C.B
L1 | 117.6 | 220 | 27.80 | 0.57 | 0.32 | 219.82 | 0.08 | 0.65 | 0.75 | 1.5 | 13
L2 | 80 | 220 | 7.30 | 0.39 | 0.08 | 219.97 | 0.01 | 0.44 | 0.51 | 1.5 | 13
L3 | 108 | 220 | 15.50 | 0.52 | 0.18 | 219.91 | 0.04 | 0.6 | 0.69 | 1.5 | 13
L4 | 108 | 220 | 21.40 | 0.52 | 0.25 | 219.87 | 0.06 | 0.6 | 0.69 | 1.5 | 13
L5 | 108 | 220 | 19.10 | 0.52 | 0.22 | 219.89 | 0.05 | 0.6 | 0.69 | 1.5 | 13
L6 | 108 | 220 | 19.40 | 0.52 | 0.22 | 219.88 | 0.05 | 0.6 | 0.69 | 1.5 | 13
L7 | 160 | 220 | 14.40 | 0.77 | 0.17 | 219.87 | 0.06 | 0.89 | 1.02 | 1.5 | 13
L8 | 700 | 220 | 177.30 | 3.37 | 0.51 | 218.29 | 0.78 | 3.87 | 4.46 | 1.5 | 13
L9 | 454 | 220 | 60.50 | 2.19 | 0.69 | 218.48 | 0.69 | 2.51 | 2.89 | 1.5 | 13

## Slide 29
The following table show the calculation summary for
Power distribution boards
DB | Total Power | Voltage | I load | I C.B | I cable | C.B | Cable Area(mm2)
DB1 | 2250 | 220 | 12.03 | 13.84 | 15.91 | 15 | 3
DB2 | 4750 | 220 | 25.40 | 29.21 | 33.59 | 30 | 10
DB3 | 4750 | 220 | 25.40 | 29.21 | 33.59 | 30 | 10
DB4 | 7750 | 220 | 41.44 | 47.66 | 54.81 | 50 | 16
DB5 | 7750 | 220 | 41.44 | 47.66 | 54.81 | 50 | 16

## Slide 30
The following table show the calculation summary for
Lighting distribution boards
DB | Total Power | Voltage | I load | I C.B | I cable | C.B | Cable Area(mm2)
DB1 | 1944 | 220 | 10.39 | 11.95 | 13.75 | 15 | 2.5
DB2 | 1672 | 220 | 8.94 | 10.28 | 11.82 | 15 | 1.5
DB3 | 1426 | 220 | 7.62 | 8.77 | 10.08 | 10 | 1.5
DB4 | 1674 | 220 | 8.95 | 10.30 | 11.84 | 15 | 1.5
DB5 | 1674 | 220 | 8.95 | 10.30 | 11.84 | 15 | 1.5

## Slide 31
The following table show the calculation summary for
Total distribution boards and Main Distribution Board
DB | Total Power | Voltage | I load | I C.B | I cable | C.B | Cable Area(mm2)
DB1 | 4193.6 | 220 | 22.426 | 25.79 | 29.66 | 30 | 6
DB2 | 6421.82 | 220 | 34.341 | 39.49 | 45.42 | 40 | 16
DB3 | 8425.82 | 220 | 45.058 | 51.82 | 59.59 | 55 | 25
DB4 | 9424.2 | 220 | 50.397 | 57.96 | 66.65 | 60 | 25
DB5 | 9424.2 | 220 | 50.397 | 57.96 | 66.65 | 60 | 25
MDB | 37889.64 | 220 | 202.62 | 233 | 268 | 235 | 120

## Slide 32
The following Figure Show the electrical distribution Board