## Slide 1: Mechanical system for Al-asria college in ramallah
Prepared by :
Hashem Ihasn Janajreh 10611602
Mohammad Abu Sarah 10613862
Sari Khaled Sobeh 10507861
Ahmad Medhat Attiyah 10614151
Supervisor :
Dr. Iyad Assaf
May-2011
بسم الله الرحمن الرحيم

## Slide 2: Presentation out line
- Building Description.
- Heating load calculation.
- Cooling load calculation.
- Duct Design.
- Plumbing System.
-fire fitting system
- Equipment Selection.
- Summary

## Slide 3: Building Description
Building Location :
Country: Palestine.
City: Ramallah
Elevation: 840 m above sea level
Latitude: 32˚.
Building face sits at the south orientation.
The wind speed in Ramallah above 5 m/s.

## Slide 4: Building details
used | Floor number
Garage | Basement -2
Operation theater major, Anesthetists, DR.s room | Basement -1
Clinics , book store, printing room ,coffee shop | Ground floor
Lecture rooms,library study | First floor
Lecture rooms,computer lab | Second floor
Simulation labs , teachers rooms , meeting room | Third floor
offices | Fourth floor
offices | Fifth floor
offices | Roof floor

## Slide 5: Heating load
    The heat loss is calculated by this equation :
Outside design condition | Inside design condition | Parameters
4 °C | 22 °C | T: temperature
62 % | 50 % | Φ : relative humidity
3 g of water/kg of dry air | 8.3 g of water/kg of dry air | W : moisture content
9 °C |  | Tun: unconditioned temperature
7 °C |  | Tg : ground temperature
Q=U*A*∆T

## Slide 6: Summary for heating load
Heating load (ton) | Heating load (kw) | FLOOR
8.45 | 29.59 | Basement (-1)
7.87 | 27.53 | Ground floor
23.48 | 82.18 | First floor
34.86 | 122.02 | Second floor
17.12 | 59.90 | Third floor
16.12 | 56.45 | Fourth floor
22.13 | 77.46 | Fifth floor
10.9 | 38.38 | Roof floor
141.01 | 493.54 | TOTAL

## Slide 7: Cooling Load
Outside design condition | Inside design condition | Parameters
32 °C | 24 °C | T: temperature
57 % | 50 % | Φ : relative humidity
17.4 g of water/kg of dry air | 9.6 g of water/kg of dry air | W : moisture content
29.4 °C |  | Tun: unconditioned temperature
7 °C |  | Tg : ground temperature
    The general conduction equation in cooling calculation is:
For transmitted through glass:
For convection through glass:
Q=UA(CLTD)corr
Q=A(SHG)(SC)(CLF)
Q=UA(CLTD)corr
CLTD correction=(CLTD+LM)K+(25.5-Ti)+(To-29.4)

## Slide 8: Summary of cooling load
Cooling load (ton) | Cooling load (kw) | Floor
10.18 | 35.62 | Basement (– 1)
12.88 | 45.1 | Ground floor
33.14 | 115.99 | First floor
45.48 | 159.18 | Second floor
19.69 | 68.90 | Third floor
22.30 | 78.06 | Fourth floor
26.37 | 92.30 | Fifth floor
13.65 | 47.76 | Roof floor
183.69 | 642.92 | Total

## Slide 9: Duct Design
Design procedures
* Number of grills and diffusers are calculated and distributed uniformly.
* The total sensible heat of floor is calculated.
* The Vcirculation of floor is calculated.
* The initial velocity for the main duct must ≤ 5 m/s.
* The pressure drop (∆P/L)=0.4 Pa/m
* The main diameter is calculated .
* The height and width of the rectangular ducts are determined from software program .

## Slide 10: Sample calculation For Design duct :
Example: first floor we choose lecture room(3)

## Slide 13: Plumbing System(potable and dranige systems)
General information:
From the table of potable water we can find the number of fixture units, the flow rate and the size as in below table :

## Slide 14
Then we can connect the water to the fixture as in the figure(example second floor):

## Slide 15
Then we calculated the number of fixture unit for all floors in the building to determined the demand of water which needed as in table:

## Slide 17: Total demand water, size for the building riser:

## Slide 18: Drainage system
As in the below figure ,we can see how can draw the drainage system on AutoCAD(Example third floor):

## Slide 19: Drainage system
We can calculated the number of fixture unit but we don’t need for a pipe of vent because the drainage pipe descent on wall and it can use a vent
The table show the number of fixture units:

## Slide 20: Drainage for rain water

## Slide 21: Drainage system
After that ,we should combine all exist drainage and going it to the manhole outside of building as in the figure:

## Slide 22: Fire fighting system
In the college we have 9 floor ,one of them is a garage which location is (second lower floor) and the 8 floor is studying floors. So we will use three systems of fire fitting which combined of them( landing valve , F.B.C, sprinklers(for garage)).
Example: third floor we use (L.v(2.5’’) , F.B.C(1.25’’)):

## Slide 23: Fire fighting
But we use the sprinkler(4’’) in garage as in the figure :

## Slide 24: Fire fighting(riser(6 in))

## Slide 25: Equipment Selection
Boiler :
From mansour catalog of steam boiler is
720 kw. MS-20 which has capacity is
Chiller :
From Petra catalog we select a model
Which has capacity is 707 kw. A P S 150 2S AC
Fan coil :
RAC 4 H/C CBP 3
400 cfm

## Slide 26: Equipment selection cont.
Exhaust fans:
From ROSENBERG program we select a fan according to total CFM for example.,
DH 355-4 D EX
PUMPS:
From LOWARA company we select
1. Circulation pump for boiler GM GS20/SV330F5T
2. Centrifugal pump for potable water GXS20-GMD20
3.Transfer pump GENYO 2HMS4/F15
4.Drainge pump DOC7VX

## Slide 27: SUMMARY
*All steps of design and plans of HVAC system are done.
*All steps of design and plans of plumping system and fire fitting system are done.
*we select a suitable equipment for the system which satisfied the required conditions.

## Slide 28
The End