## Slide 1: Energy Audit for Engineers Association Building - Nablus.
An-Najah National University
P R E P A R E D B Y : H A S H E M G H A N E M
M A H M O U D I S M A I E L Y A S I N Y A S I N
S U P E R V I S O R :
D R . M O H A M M A D A L S A Y E D

## Slide 2: Agenda
1
Introduction
2
Softwares Used
3
methodology
5
Conclusion Recommendations
4
Results and Discussion
1

## Slide 3: Introduction
Preview of Project 1
Objectives
The current status of the EAB
2

## Slide 4: Preview of Project 1
Analyzed the building's electrical bills
Examined the lighting systems Reviewed the architectural plans
3

## Slide 5: Objectives
1
Modifying the lighting system inside the Association
2
Study the HVAC system and find savings opportunities for the system
3
Design a solar system for the Association
4

## Slide 6: Softwares Used
AutoCAD
HAP
(Hourly Analysis Program)
PVsyst
5

## Slide 7: Methodology
01 Study the EAB behaviour and its energy bills
Using the HAP program to simulate the building’s energy bill and assume different case scenarios to study how the energy bills diffrentiate for each scenario
Using the PVsyst program to design a solar cell system (on-grid and hybrid) and decide which of these systems is economically mo feasible.
02
03

## Slide 8: Results and Discussion

## Slide 9: E A B O P E R A T I N G A T N O R M A L C O N D I T I O N S
Cooling 37.3%
Lights 32.8%
Electric Equipment 18.6%
Heating 8%
Air System 3.3%
Total Cost
NIS/year
24,757
Total
kWh/year
36,568

## Slide 10: E A B O P E R A T I N G A T F U L L L O A D
Lights 36.7%
Cooling 33.4%
Heating 5.4%
Air System 2.5%
Electric Equipment 21.9%
Total Cost
NIS/year
37,211
Total
kWh/year
54,964

## Slide 11: E A B O P E R A T I N G A T T = 2 3 ⁰ C
Lights 37.8%
Cooling 29.8%
Electric Equipment 21.5%
Heating 9.2%
Air System 1.7%
Total Cost
NIS/year
21,448
Total
kWh/year
31,680

## Slide 12: F O R N O H V A C I N A P R I L A N D N O V E M B E R
Lights 34.4%
Cooling 31.3%
Electric Equipment 22.7%
Heating 9.8%
Air System 1.8%
Total Cost
NIS/year
20,295
Total
kWh/year
29,977

## Slide 14
13

## Slide 15: Solar System
Grid-Connected (On-Grid) System
Off-Grid Systems Hybrid Systems

## Slide 17
16

## Slide 18
17

## Slide 19
Conclusion
and
Recommendations
18

## Slide 20: Our Savings
15%
2.67%
12.31%
12.31%
Savings Percentage of optimizing the Temperature
Savings Percentage of installing a Canopy
2.67%
Total Savings Percentages
15%

## Slide 21: 1.The building is not running on full capacity.
The lighting system should be fixed.
Turning off the HVAC units in April and November and setting the Temperature at 23, will decrease the EAB’s energy bill by about 15%.
4. On-Grid solar system proved to be more feasible and suitable for the EAB.
5.If the recommendation were taken into consideration, the energy bill decrease by about 20% of their last bill.

## Slide 22: THANKS FROM OUR TEAM
Mahmoud Ismael
Energy Engineer
Yasin Yasin
Energy Engineer
Hashem Ghanem
Energy Engineer