## Slide 1: Design of a Wastewater Collection Network for Kofur Laqif along with Cost Estimate and Assessment of Potential Alternatives for Locations of Wastewater Treatment Plants
Prepared by
Mariam Jaber
Supervisor
Dr. Mohammad N. Almasri
2017

## Slide 2: Outlines
Introduction
Objectives
Study Area
Methodology
Results

## Slide 5
Objectives
To design a wastewater collection network for a part of kofur laqif Village using Sewer CAD.
& calculate the cost
&location of Wastewater Treatment Plant

## Slide 6
Study Area
350
245
West, N
East, Q
1997
699
2007
856
r= 2.01%
7692 m3/mon

## Slide 7
Methodology
Determine problem
Selection of study area
Data Collection
Loads
Determination
Design WWCN
1
2
3
4
5
6
7
Cost Estimation
Location of WWTP

## Slide 8: Data collection
Data
AutoCAD
Village Council
Contour
GIS
Village Council
Population
word
PCBS
Communities
GIS
Dr
Settlements
GIS
Dr

## Slide 9: Network

## Slide 10: Load calculations

## Slide 13
P =2250 c
Total Load = MH. Load of WW generation + MH. Load of Infiltration
For MH-20:
Total load = (1388.89*2250/242381.82933)*0.15*0.8*4
+ 0.2*(1388.89*2250/242381.82933)*0.15*0.8
= 6.498 m3/d

## Slide 14
Design constrains
Velocity
Cover
Slope
0.6-3m/s
1-5m
1-15%
Partial flow
80%

## Slide 16
Chart: The slope of the pipe
Chart: The cover of the pipe
Chart: the velocity of the pipe (m/s)

## Slide 17
Chart: The cover of the pipe
Chart: The cover of the pipe
Before
After

## Slide 18
Data profile

## Slide 22
Excavation
For 8 in pipe
Cost/m³ | Cost ($)
1 | 12

## Slide 23
Pipes
Diameter (in) | Unit price ($)
8 | 13
10 | 18
12 | 40

## Slide 24
Manholes
MH element | Dimensions | Cost
Base | 100×60 | $99
 | 100×80 | $115
Cone | 100×75 | $99
Cover | 100×20 | $61
Ring | 100×30 | $54
 | 100×40 | $56
 | 100×50 | $57

## Slide 25
Asphalt
Unit Price ($) per 1 m2 | 18

## Slide 26
Chart: 
 | 225105.3 | 83202.83 | 69227 | 49221

## Slide 27
Wastewater Treatment Plant Location