## Slide 1: Improvements of Sarra Treatment Plant
Prepared by :
Doa’a Jawabri
Asma Turabi
Ruba Mansour

## Slide 2: Wastewater disposal
Wastewater collection systems.
Cesspools.

## Slide 3: Constructed Wetlands
Artificial lands.
Wastewater sources.
Use natural processes.
Low cost.
Slow rate of operation.

## Slide 4
Location & Pop
SARRA
Water Resources
Wastewater Disposal
Land use
Climate
Sewer Network

## Slide 5
Exit
Entrance
back
Southwest of Nablus.
Population 3042 capita.
N

## Slide 6: Climate
Average annual rainfall 451 mm.
Average Temperature 18˚C.
Average Humidity 59%.
Wind 10 km/hr.
back

## Slide 7: Land use
Total area : 50000 donums .
4000 donums agricultural area :
permanent crops
Range lands
Arable lands
back

## Slide 8: Water Resources
back
Water Network
Established in 2009.
Covers 90% of houses.

## Slide 9: Sewer Network
Established in 2004 and run in 2014.
Covers 96% of Sarra
back

## Slide 10: WW Treatment Plant
Established in 2013.
Functioning as subsurface Wetlands.
After primary settling.
Area 10 donums.
Australian Qossaip plants is used.
With two stages of treatment.

## Slide 11: Plan of Treatment Plant

## Slide 12: Stages of Treatment
Hydraulic profile

## Slide 13: Objectives
To know if treatment plant is working well.
Fix problems.

## Slide 14: Methodology
Nine samples were taken and experiments were done including:
BOD
COD

## Slide 15: Site visit and samples collection

## Slide 16: Experiments

## Slide 17: Results of Experiments

## Slide 18: Standards used for checks
TR34 Palestinian Standards.

## Slide 19: BOD & COD Checks
Meets standard or not | Palestinian Specifications |  |  |  | Sarra | Chemical Properties (mg/L)
 | D | C | B | A |  | 
 | 60 | 40 | 20 | 20 | 79 | BOD
 | 150 | 100 | 50 | 50 | 111 | COD

## Slide 20: Reed Model
Reed model was used to find k20 for two stages.
KT : is a rate constant at the wetland temperature .
The flow entered the inlet of treatment plant is 238.7 m3/day.

## Slide 21
K20 and Efficiencies were found for the two stages.
 | BODi | BODo | ln(BODi/BODo) | Area(m2) | Y(m) | N | Q | KT | K20 | Efficiency
VS | 335 | 225 | 0.398 | 250 | 0.6 | 0.85 | 39.66 | 0.123 | 0.098 | 32.835
HS | 225 | 156 | 0.366 | 500 | 0.6 | 0.85 | 39.66 | 0.0569 | 0.045 | 30.666

## Slide 22
Comparison between VS & HS
 | KT at t = 24° C | K20 | Reference value | Comment
Vertical stage | 0.742 | 0.588 | 1.104 | 
Horizontal stage | 0.341 | 0.270 | 1.104 | 

## Slide 23: Design Alternative
UASB tank:
  Upflow Anaerobic Sludge Blanket Reactors.
  In Primary treatment.
  After Screw screens.
  hydraulic retention time 6-12 hrs.

## Slide 24: UASB tank
Anaerobic conditions.
Sludge blanket.
GLS (gas liquid
separators).

## Slide 25: Analysis and Design
Wastewater simulation Program was used : GPS-x.

## Slide 26
Case 1
UASB

## Slide 27
Case 2
UASB- Digester.

## Slide 28: Manual Design
Primal design was made to enter approximate values to each tank in GPS-x including:
Volumes
Areas
Depths

## Slide 29: Data entered
Influent composition

## Slide 30: UASB data

## Slide 31: Outfall results for the two cases :
Physical and Chemical Properties (mg/L) | Simulation results(mg/l) |  | Palestinian Standards (mg/L) |  |  |  | Meet standards or not? | 
 | Case1 | Case2 | A | B | C | D | Case1 | Case2
TSS | 5.52 | 91 | 30 | 30 | 50 | 90 |  | 
BOD | 280 | 24.2 | 20 | 20 | 40 | 60 |  | 
COD | 430 | 74 | 50 | 50 | 100 | 150 |  | 
Ammonia N | 0.99 | 1.27 | 5 | 5 | 10 | 15 |  | 
Soluble PO4-P | 0.8 | 2.7 | 30 | 30 | 30 | 30 |  | 

## Slide 32
Case 1 needs wetlands after it but case 2 doesn’t.
The concentration of BOD when using wetland after case1

## Slide 33: Checks for HRT
Tank Type | HRT (from simulation results) | Typical value for HRT
Primary clarifier | 1.64 hr | (1-2) hr 
Secondary clarifier | 3.13 hr | (2-4) hr 
UASB | 7.77 hr | (8-10) hr 
Anaerobic digestion 1 | 1.2 days | (1-2)day 
Anaerobic digestion 2 | 2.33 days | (1-2) day 
Thickener | 2.28 days | Min T=0.35 day

## Slide 34: Check for Vo(Primary Clarifier)

## Slide 35: Check for Vo(Secondary Clarifier)

## Slide 36: Check (SLR) for Thickener

## Slide 37: The two cases efficiencies

## Slide 38: Conclusions
Original case: overloaded.
First case : improve efficiency.
Second case : higher efficiency and no need for wetlands.

## Slide 39: Recommendations
Provide area for the project.
Cost Analysis.
Maintenance of TP.
Use water for irrigation.
Good pipes for treated water.

## Slide 40
Thank you
For
listening!