## Slide 1
Chapter six
Dynamic loads
6.1: Design response spectrum for the structure.
6.2: The dynamic analysis method used.
6.3: Hand calculation for lateral seismic force.
6.4: SAP calculation for lateral seismic force.
6.5: Z component for earthquake.

## Slide 2
6.1: Design response spectrum for the structure:
-Z=0.2 g
-site class = B
(for rock)
-S1=1.25*Z=0.25
-Ss=2.5 Z =0.5

## Slide 3
Now, Fa=1 and Fv=1 for site class B and S1 and Ss values

## Slide 4
SMs=Fa*Ss=0.5…… SDs=SMs=0.5
SM1=Fv*S1=0.25.... SD1=SM1=0.25

## Slide 7
Design response spectrum for rock soil and intermediate frame

## Slide 8: The dynamic analysis method used :

## Slide 9: Hand calculation for lateral seismic force: T=from Reyluph method=2π(ƹ(m*∆2) /ƹ(F*∆))0.5 Mass for each story =(SID+DEAD+WALL)/7*9.81=32293+13170+10000/7*9.81=807.6 TON apply 1 kN/m2 for each slab in each floor in the x direction

## Slide 10: T =2π(7.74/95,4).5=1.79 sec. Error=((1.79-1.92)/1.92)*100% =6.7%<20% …….ok
Cs=0.071/1.79 =0.04

## Slide 11
From SAP reactions we find the weights:
F=Cs*W
= 0.04 *( Dead+SID+Wall)
=0.04*(32293+13170+10000)
F x = 2218.5kN
F y = 2218.5kN

## Slide 12
SAP calculation for lateral seismic force:
E=ϼEh + Ev ………….. (ϼ = 1.3)
Eh=EX+EY
EX=Ex+0.3Ey
EY=Ey+0.3Ex
Ev = 0.2* SDs *D

## Slide 13
The new combination will be :
1) 1.2 D +1.6 L
2) 1.4D
3) 1.3 D + 1.0 L +1.3 EQ
4) 1.3 D + 1.0 L -1.3EQ
5) 0.8D + 1.3E Q
6) 0.8 D – 1.3 EQ

## Slide 16: After modifying the scale factors the values from SAP now is ok:
Fx SAP*scale factor x=Fx manual
So :
scale factor x=(Fx manual/FxSAP)*(old scale factor=2.8).
=(2218.5*2.8)/1933.5=3.21.

## Slide 17: Modal mass participation ratio:

## Slide 18
Chapter seven
Design and Detailing
Contents:
7.1: Final sections.
7.2:check Drift.
7.3: Design of slabs.
7.4: Design of beams.
7.5: Design of columns.
7.6: Design of mat foundation.
7.7: Design of shear wall.

## Slide 19
7.1: Final Sections:

## Slide 20: 7.1.1: For slabs:

## Slide 21: For Beams:

## Slide 22: The Beam dimensions :
Beam NO | Width | Depth
B1 | 750 mm | 300 mm
B2 | 1200 mm | 300 mm
B3 | 1250 mm | 300 mm
B4 | mm | 300 mm
B5 | 1600 mm | 350 mm

## Slide 23: For Columns:

## Slide 24: The Column dimensions :
Column NO. | Width (mm) | Depth(mm)
Column 1 | 1000 | 1000
Column2 | 850 | 800
Column3 | 700 | 600
Column4 | 600 | 500

## Slide 25: 7.2 Check Drift :
∆max = 0.02*h H for each story = 3000 mm ∆max = 0.02*3000 = 60 mm

## Slide 26
Deflection of 7th floor = 6.7 mm.
Deflection of 6th floor =11 mm.
Deflection of 5th floor= 6.5mm
Deflection of 4th floor = 11 mm.
Deflection of 3rd floor = 12.1 mm.
Deflection of 2nd floor = 12.9 mm.
Deflection of 1stfloor =13.5 mm.
The critical case at the first floor.
ΔS(max) = 13.5 mm.
Maximum limitation = 0.02* 3000 = 60 mm.
13.5 mm< 60 mm ………..OK

## Slide 27
7.3: Design of slabs:
ϼmin= max 1.4/Fy=(0.0033)
0.25*fc.5/Fy=(0.0029)
=0.0033.
As min=0.0033*bw*d=0.0033*130*270=115.83 mm2.

## Slide 28
For the slabs which is in the y direction (M22):
-ve moment (kN.m/m) as shown

## Slide 29
+vemoment(kN.m/m) as shown .

## Slide 30
For the slabs which is in the x direction (M11)
-vemoment(kN.m/m) as shown

## Slide 31
+vemoment(kN.m/m) as shown

## Slide 35
Beam Detailing:
-According to the code intermediate design detailing shall satisfy the following requirements:

## Slide 36: For Beam 6:

## Slide 37: Beam 6 Detailing :

## Slide 38: For Beam 22 :

## Slide 39: Beam 22 Detailing :

## Slide 40
7.5: Design of columns:

## Slide 41
column 1 detailing
c2 section detailing
column 3 section detailing.
column 4 section detailing

## Slide 42
Column Detailing:
According to the code intermediate design detailing shall satisfy the following requirements:

## Slide 44
and the final longitudinal section for C1 shown

## Slide 45
Check SAP results:
We check the sap results for the column shown below

## Slide 48
We notice that ϼ<1% for both values of Ɣ(.9 and.75) so its ok for
Ɣ=.88=1000-2*(cover=60)/1000.
As we notice from the previous Figure that our columns are too much below ϼ min.

## Slide 49: 7.6: Design of mat foundation:
The plane view of mat foundation.

## Slide 50: -Loads on mat foundation:

## Slide 51: -Concrete B350 is used for mat foundation :

## Slide 52: We assume thickness of mate foundation equal 700 mm
Sub grade modulus =K*Q allowable= 100*400= 40000 kN/m3

## Slide 53: -Checks of the footing :
Compatibility:

## Slide 54: -Deflection :
By SAFE:
Max deflection from SAFE is 9.4 mm.
By hand:
Δ allowable = qall/K= 400/40000= 0.01 m= 10 mm.
Δ allowable > max deflection .............. So it's ok.

## Slide 55: - punching shear: By SAFE:
We notice that no punching shear occurs, because the ratio of bunching shear is less than one.

## Slide 56: By hand:

## Slide 57: First area: Interior column pu from sap = 4374 kN. ΦVcp=0.75*(1/3)* *(4*1630)*630*10-3. =5433.85 kN>>pu............. So it's ok.
Second area: Corner column.
pu from sap = 1164 kN.
ΦVcp=0.75*(1/3)* *(2*1015+2*915)*630*10-3.
=3216.97 kN>>pu ............. So it's ok.

## Slide 58: Third area: Edge column pu from sap= 2907 kN ΦVcp=0.75*(1/3)* *(2*1165+2*1430)*630*10-3. =4325.4kN>>pu............. So its ok.
Reinforcement
As min=ρ*b*d.
=0.0018*1000*(700-70)=1134 mm2.
So we use 8Φ14/m.
We notice that reinforcement in all region is less than Asmin so that we use Asmin.

## Slide 59: 7.7: Design of shear wall:

## Slide 60: -Designing SW NO. 1:
Lw=4 m.
hw=3m.
h=0.2m.

## Slide 61: Flexure design: Finding the moment and force values.

## Slide 62: The result : Use 20 Ф25
Shear Design:
Vc ≤ A cr
Acr = horizontal cross-sectional area of the wall.
Vcv= 200*4000*10-3 = 705.5 kN
ФVcv= 0.75*705.5 = 529.125 kN
Vu = 19.1 KN

## Slide 63: Ρh = 0.002 for bars db ≤16 mm Ρv = 0.0012 for db ≤16 mm
AS horizontal = 0.002*200*1000 = 400mm 2
Use 6Ф10 / m ……… 2 Layers 3Ф10/m
AS vertical = 0.0012*200*1000 = 240mm 2
Use 4Ф10 / m ……… 2 Layers 2Ф10/m

## Slide 64: - Check D+L:
PD= DL+SI +shear wall weight+ wall load
Shear wall own weight = 420 kN.
1.2DL+1.6LL = 2796.5= kN.
Фpn = 0.65*0.8*(0.85*fc*Ac+fy AS)
= 11550 kN ≥ 2796.5 ………OK

## Slide 65: - Check stability:

## Slide 66: - Check Drift:
ΔS= 0.01 mm
Δm = Um = 0.7*R ΔS
= 0.7*3.5*0.01= 0.0245
Δ all = 0.002*h = 0.002*7*3= 0.042 mm ≥ 0.0245 …… OK

## Slide 67: - Detailing for shear wall:

## Slide 68
ريم : الترحيب+(1-8)
ملك(9 -15)
علا ( 16- 22)
ملك (23+24)
بنان ( 25-32)slaps
ريم (33-37)beams
بنان (38-42)
علا (43-56)
ملك (57-62)
ريم63) -65)

## Slide 69: سلايد 60 مشكله
سلايد 63 مشكله
سلايد 32 في حد بدو يضيف عليه اشي ولا لا ؟؟؟؟؟؟؟؟؟؟؟؟؟؟؟